## Slide 2: Lessons learnt and new concepts for conventional Safety in FCC
André Henriques, Saverio La Mendola
FCC Week 2015
26th March 2015
For a general overview:
R. Trant, “Health, safety and environment, FCC Kick-off”
http://cds.cern.ch/record/1694672

## Slide 3: Overview
Focus on studies for conventional Safety aspects:
  Air management[1] 2. Cryogenic Safety 3. Evacuation
Studies focused on two main tunnel cross-sections FCC-hh:
  4.5 m Ø double tunnel
Outcome is in line with RP constraints
  6 m Ø single tunnel
[1] Air Management for RP
See M. Widorski presentation

## Slide 4: Air management functions
Provide fresh air during access
Cope with different accidental scenarios (e.g. fire, Oxygen Deficiency Hazard, gas leak)
Provide dynamic confinement between “machine zone” and “safe zone” for protection of occupants in accidental scenarios
Provide dynamic confinement between “controlled” areas and areas accessible during run for protection of occupants
Provide sufficient air flow for heat removal during operation

## Slide 5: Air management concepts
Longitudinal ventilation (LV):
Main Advantages, w.r.to conventional Safety | Main Disadvantages, w.r.to conventional Safety
Provides fresh air for occupants during access Regulate air speed in the tunnel | Propagation and contamination of smoke to others volumes of the tunnel Even if the ventilation is stopped , the smoke still propagates
Smoke propagation in LV:
Courtesy of S. La Mendola
See also the presentation «A simplified model for tunnel fire dynamics predictions» by S. La Mendola EDMS 1278776

## Slide 6: Air management concepts
Transverse ventilation (TV):
Main Advantages, w.r.to conventional Safety | Main Disadvantages, w.r.to feasibility of the system
Limit the propagation and contamination of smoke to others volumes of the tunnel Provide dynamic confinement localized near the fire | Large ducts are needed  occupy ~50 % of the tunnel volume Larger tunnel needed
Smoke propagation in TV:
Fresh air supply duct
Vitiated air exhaust duct
Normal operation
Fresh air supply duct
Vitiated air exhaust duct
Fire conditions
Ø 7.5 m
D = 7.5 m  Atotal = 44 m2  Auseful = 34 m2
Aducts = 14 m2 
41 % of the useful area
Notes: In case of fire, a transverse ventilation system limits the propagation and contamination of smoke to other volumes of the tunnel. Additionally, it provides dynamic confinement localized near the fire.
However, it needs large ducts that occupy about 50 % of the tunnel volume. This also results in increased tunneling costs.

## Slide 7: Air management concepts
“Optimised” solution:
Longitudinal Ventilation for normal operations
  Provide the requirements for occupational health (Fresh air)
  Dedicated smoke extraction system
  Limit propagation and contamination of smoke to others volumes of the tunnel
  Provide the dynamic confinement
  Reduced cross section of the smoke extraction duct

## Slide 8: Smoke extraction system
Example of a section of the FCC tunnel:
  Nominal conditions
…
Shaft
Tunnel
Dedicated smoke extraction duct
Smoke control dampers
LV for Fresh air
Dedicated smoke extractor

## Slide 9: Smoke extraction system
Example of a section of the FCC tunnel:
  Accidental scenario – e.g. Fire
  Longitudinal ventilation is stopped
  Smoke extraction is ON
Length of Smoke Compartment
…
Dynamic Confinement

## Slide 10: Smoke extraction system
Fire Detection system:
  Shall be able to identify the fire location within a certain length, to ensure that the dampers open in the correct location
Length of Smoke Compartment
…

## Slide 11: Smoke extraction system
Fire Detection system:
  Shall be able to identify the fire location within a certain length, to ensure that the dampers open in the correct location
Length of Smoke Compartment
…

## Slide 12: Smoke extraction system
Fire Detection system:
  Shall be able to identify the fire location within a certain length, to ensure that the dampers open in the correct location
…
Length of Smoke Compartment

## Slide 13: Smoke extraction system - Simulations
Full confinement within the 200 m compartment for a 1 MW fire and 12 m3/s
Smoke compartment = 200m
Extraction flowrate = 12 m3/s
Smoke curtain (in addition)
Full confinement within the 200 m compartment for a 2 MW fire and 12 m3/s
This system provides a good smoke confinement also in off-nominal conditions
H = 5 m
h = 2 m
Smoke curtain
H - h = 3 m
Courtesy of S. La Mendola
Notes: 12 m3/s  43000 m3/h
With 36 m3/s we wont need curtains

## Slide 14: Pressure drop – Curtains
Ø 6 m tunnel
Curtain: Fixed part
Length = 10 km
Air flow = 140 000 m3/h (1 ACH)
Dh = 4.2 m
 | # | ΔPfixed [Pa] | ΔPcomplete [Pa]
Curtains | 1 | 13.5 | 109
 | 50 (1 per 200m) | 675 | 5450
 | 20 (1 per 500m) | 270 | 2180
Feasible from pressure drop point of view
Roller curtain
Fixed curtain
Tunnel  ΔP = 136 Pa
Notes: Full curtain 5400 Pa

## Slide 15: Smoke extraction system
Extraction duct Ø 1.2 m
Extraction flow rate of 12 m3/s;
Velocity in duct of 10 m/s;
Considering:
Requires an extraction duct of 1.2 m
Roller curtain
Fixed curtain
Can this system be used for other purposes?

## Slide 16: Cryogenic Safety – ODH
Can the smoke extraction system also cope with a potential He release?
Based on LHC, we have 2 scenarios:
Access (no powering): few hundred g/s
 Compatible with smoke extraction proposal (12 m3/s)
No access (beam mode / magnets powered): couple tenths kg/s
 By far not compatible with smoke extraction proposal (12 m3/s)

Smoke extraction system  Emergency Extraction system (EES)
Notes: Linked to a Maximum Credible Incident

## Slide 17: Evacuation
6 m Ø Single Tunnel
Evacuate through a door leading to a “Safe Zone”:
Fire resistant
Air tight in case of cryogen release
Overpressure, w.r.to machine zone
Personnel transportation for evacuation
Safe zone with limited amount of combustible material
Notes: Evacuate through a door leading to a “Safe Area” within or part of the same tunnel, but separated in view of

## Slide 18: Evacuation
4.5 m Ø Double Tunnel
Evacuate through a passage way connecting to a “Safe Zone” in the parallel tunnel:
Fire resistant
Air tight in case of cryogen release
Overpressure, w.r.to machine zone
More space for transportation and for emergency intervention teams
If access to // tunnel during powering  “Pressure resistant” doors
ΔP major release

## Slide 19: Evacuation

Dimensions for Safe Area in front of the lifts
Assumptions (rough scaling from LHC):
Maximum occupants x3
Accidental scenario
Uniform distribution in arc
…
Data:
Lifts in machine shaft: 1 lift capacity of 30 people; velocity of 5 m/s; stroke 300m
Arc length 8 km
Evacuation speed: 2.5 m/s (9 km/h)
Courtesy of S. La Mendola
Similar areas as for the LHC today
Notes: Clearly state the assumptions (x3)
30 people/min (fcc)
20 people/min (lhc)
Other assumptions:
- Occ.s don’t interact between each other
Walking speed is constant var. Gaus distribution
Pre-movement time = 0s (occ start moving at t=0s)
Every occ moves with the same transportation mean (“RTL”)

## Slide 20: Conclusions
Air Management:
Smoke curtains:
Cryogenic Safety:
Evacuation:
Cross-section:
Longitudinal ventilation  nominal operation
Emergency Extraction system (EES)  accidental scenarios
Release in access mode  can be handled by EES
During powering  “pressure resistance” towards Safe Area
Optimized  Fixed + Roller part
Separate hazards from Safe zone
Dimensions of Safe area near lifts  further studies but comparable to LHC
Double tunnel has advantages for Safety and accessibility
Feasible solution w.r.to pressure drop
Notes: emergency intervention teams (Fire Brigade)

## Slide 21: Further Studies
Additional simulations for the EES  optimisation
Pressure build-up in case of major helium release (no access)
Impact on the mechanical properties of the ventilation system (ducts, supports, etc.), due to the low temperatures
  Optimise sizing of cryogenic relief devices – Kryolize Project
  Optimisation of the transportation mean and layout for evacuation
Evacuation scenarios for surface area in front of lifts
Prepare environmental impact study
Support all FCC WGs on Safety issues

## Slide 22
Thank you very much
for your attention
Acknowledgements:
C. Cook, S. La Mendola, P. Lebrun, M. Nonis, J. Osborne, I. Ruehl, L. Tavian, R. Trant, M. Widorski

## Slide 24: Spare Slides

## Slide 25: Cryogenic Safety – ODH
Access Mode:
Release scenario of ~1 kg/s
Aid evacuation
margin
Smoke extraction proposal OK to extract 1 kg/s He release, w.r.to flow rate capacity  min margin by factor 2
Study the impact on the mechanical properties of the ventilation system (ducts, supports, etc.), due to the low temperatures


## Slide 26: Cryogenic Safety – ODH
No Access “Beam Mode”:
Release scenario of ~ 30 kg/s (assumption from LHC)
After 18 K, Q due to He leak > Q smoke extraction
Smoke extraction proposal will, by far, not be possible to cope with MCI, but:
No access
Protect installation

## Slide 27: Cryogenic Safety – ODH
~ Sectorise the QRL each 2 cells ~ 2*100m
6 L LHe / m  5200 L LHe @ 300 K  3640 m3 GHe
FCC SACR: 3.2 km (most conservative)
No Access “Beam Mode”:
Release scenario is 32 kg/s (assumption from LHC)
6 m Ø : 14 m2
4.5 m Ø : 11 m2
4.5 m Ø  43100 m3 of air + 3640 m3 GHe  154 mbar pressure increase
6 m Ø  33700 m3 of air + 3640 m3 GHe  120 mbar pressure increase

## Slide 28: Cryogenic Safety – ODH
6 m Ø
ΔP = 120 mbar
In LHC (MCI): from 30 to 200 mbar
Ref: Report of the Safety task force, 2009
4.5 m Ø
ΔP = 154 mbar

## Slide 29: Cryogenic Safety – ODH
He Spill Test in LHC: Temperature for 340 g/s GHe release
Temperature +0.5m
above the outlet
Stable at 250 K
after 5min
Courtesy of T. Koettig TE/CRG, CERN
Discharge

## Slide 30: Evacuation

Dimensions for Safe Area (in front of the lifts)
Assumptions (rough scaling from LHC):
Maximum occupants, accidental scenario
Evacuation from experiments:
60s < t < 600s
Uniform distribution in arc: ~4 occ. / 100m
Data:
Lifts in machine shaft: 1 lift capacity of 30 people; velocity of 5 m/s; stroke 300m
t = 0 s (evacuation alarm)
Arc length 8 km
Evacuation speed: 2.5 m/s (9 km/h)
Courtesy of S. La Mendola
Safe Area in PM shaft
300 people (arc)
300 people (Exp. Cavern)
150 people (LSS+UL+PM)
Notes: Clearly state the assumptions (x3)
Other assumptions:
- Occ.s don’t interact between each other
Walking speed is constant var. Gaus distribution
Pre-movement time = 0s (occ start moving at t=0s)
Every occ moves with the same transportation mean (“RTL”)

## Slide 31: Evacuation
Dimensions for Safe Area
Courtesy of S. La Mendola
3 ≤ d ≤ 4
Tolerated only
for very short periods
d < 3
Acceptable
d > 4
Not acceptable
Nominal value 3 persons/m2
4 persons/m2
Scenario 1: alarm during maintenance of the experimental (PX) lift
130 m2
Safe Area
Scenario 2: alarm during maintenance in the PX lift
Limit the occ. In the exp. Cavern by ½
80 m2
Safe Area
Areas same order of magnitude as for the LHC today.

## Slide 32
Maximum admissible crowding in safe zones
3 persons/m2
4 persons/m2
3 ≤ d ≤ 4
Tolerated only
for very short periods
d < 3
Acceptable
d > 4
Not acceptable
Nominal value 3 persons/m2
4 persons/m2
Art. L 3 of the ERP regulation fixes a maximum crowding of 3 persons/m2 for people attending an event in a room without chairs or benches.
Chart: Speed vs. occupant density (BS PD 7974-6:2004)
| 0.0 | 1.0 | 2.0 | 3.0 | 3.7 | 3.8 | 4.0 | 5.0
Speed [m/s] | 1.4 | 1.0276 | 0.6552 | 0.2828 | 0.02212 | 0 | 0 | 0
These figures have been tested for a number of fire scenarios.
At 3.8 persons/m2 movement ceases