## Slide 1: Electronic challenges in ITER Towards high-availability applications
Bruno Soares Gonçalves,
A. Batista, M. Correia, J. Sousa, B.B. Carvalho, B. Santos, A. Duarte, A. P. Rodrigues, R. Pereira, P.F. Carvalho, A. Fernandes, A. Combo, N. Cruz, C. Leong, A.R. Ramos, J. P. Santos, J. G. Marques, I. C. Teixeira, J. P. Teixeira
Partners

## Slide 2: Control in fusion plasmas is critical for safe operation and to achieve high performance
Density
control
Magnetic control
position, shape & vertical stabilization
Wall protection
Instabilities mitigation
& control
Notes: r

## Slide 3: Nuclear Fusion control systems are highly complex
Density
control
Magnetic control
position, shape & vertical stabilization
Wall protection
Instabilities mitigation
& control
Malfunction of a single component may originate relevant damage to entire infrastructure
Notes: r

## Slide 4: When something fails… on position control
Notes: Example of jet disruption due to loss of vertical stabilization

## Slide 5: On ITER similar events will cause huge thermal loads on Plasma Facing Components
Will require a far higher level of availability and reliability than previous/existing tokamaks
.
30-60 MJ/m2 for ~0.1s
EM loads
~20-45 MN
~90 MN
  PFCs cannot be designed to sustain such (repetitive) thermal loads

## Slide 6
RAMI analysis for ITER
Inherent Availability Ai = 60%
Operational Availability Ao = 32%
Availability goal in Fusion – similar to Nuclear Fission (70-80%) at full power
R. Buende, Fusion Engineering and Design 29 (1995) 262-285
D. van Houtte et al. / Fusion Engineering and Design 86 (2011) 680–683
Notes: Necessary to build our C&DA system from inst. Standards which provide HA

## Slide 7: Steady-state operation calls for High Availability
Risk reduction
Resilience to failure
Sensors - backup set
Redundant acquisition channels
Fault detection & mitigation
99.999% up-time (reference for HA), correspond to ~5 minutes of down-time per year
Requires the use of robust instrumentation standards designed for high availability!

## Slide 8: Example | ITER roadmap for fast controllers according to ITER Plant Control Design Handbook (PCDH)
Category
Technology
I&C
DAQ
DAQ
PCIe/PXIe
MTCA.4/mTCA
ATCA
Slow Controller
(PLC) I&C applications
Fast Control
I&C
Interlock
Diagnostics
Data acquisition
Demanding diagnostics, I&C and Interlock tasks
e.g Plasma Control
Control loop frequency, Processing power network capacity, Real-time constraints, Complexity, Price, Availability

## Slide 9: ATCA standard is already designed for high availability & high throughput
Redundant controller
Redundant power supplies
Redundant fans
Redundant backplane interconnect
Redundant Shelf managers

## Slide 10
IPFN ATCA subsystem overview
ATCA shelf
Digitizer
node slots
PCIe endpoints
Data & Timing Switch
hub slots
PCIe switch
Host interface
Timing switch
Timing sync
PCIe cable
PCIe host

## Slide 11: ATCA galvanic isolated digitizer node board for MIMO Systems | high channel density & modularity
*added to ITER catalogue of I&C products
RTM
IPFN’s ATCA-IO-Processor*
ADC module , 1-2 MSPS, 18 bit
with ADC x2 and chopper mode
DAC module
with DAC x2
PICMG 3.0/3.4 & AXIe compatible
48 analog inputs, outputs or a combination of both
Notes: ATCA-MIMO-ISOL board
modular

## Slide 12: ATCA-IO-Processor | Anatomy
Virtex 6
CF Card
DDR memory
IPMC
IO modules
(customizable)
RTM
(passive)
Optical or elecrical SFP interface
(Full duplex)

## Slide 13: Hardware (shelf & board) continuous monitoring
IPMC
RTM Passive
Hardware Monitoring
CoreIPM OPMA2368 Module

## Slide 14: RTM I/O connectivity for “Hot Swap”

## Slide 15: Hot-swap allows runtime replacement
Pull fixing handle to remove board
2
IO board on ATCA slot
1
Push handle to fix board
Board detected and ready for use!
3

## Slide 16
IPMC
Hot-swap allows runtime replacement
Handle Switch
ShM
ShMC
IPMB-0
Payload Power
network
BLUE LED
ShMC
PCIe
@ hardware level
Insertion/extraction of ATCA modules with use of Handle switch
IPMC negotiates with ShM payload power ON/OFF for safe module insertion/removal
BLUE LED signals to operator if board may be inserted/removed
@ software level
Corresponding PCIe devices need to be inserted/removed at software layers
Applications using/communicating with PCIe slots need to be successfully opened/closed
Set relationship between ATCA Hot Swap and PCIe Hotplug (software device insertion/removal) | also being developed by IPFN
Notes: ATCA Hot Swap solves the problem of insertion-extraction of blades at the hardware level. Basically controlling the power that is given to the slot and managed by the IPMC to the blade Payload Power network
But - what happens at the software level? At the PCI Express network - we haven’t yet mentioned too much about it. There is a good reason for it.

## Slide 17: DMA Channel implementation allows changing output rate dynamically according to external events distributed through SDN
DMA #1 Real-time data at programmable sampling rate
DMA #2 Data for archiving at programmable sampling frequencies
DMA #3 Data for continuous storage on the onboard memory
All data time-stamped before sent through DMA channel.
Circular buffer

## Slide 18
ATCA AMC Carrier / Hub ATCA-PTSW-AMC4*
PCIe on fabric not available from industry
Support multiple processors on AMC slots or external through PCIe cable connection
Mid/full-size COTS AMC modules can be installed
FPGA for timing & synchronization IEEE-1588 to IRIG on backplane + 100 MHz clock
AMC
AMC
AMC
AMC
IEEE-1588
PCIe host x16
IPM controller module
FPGA for timing & synchronization IEEE-1588 to IRIG on backplane + 100 MHz clock
*added to ITER catalogue of I&C products

## Slide 19: ATCA backplane synchronization | signals distribution
Data time stamping using IRIG time distributed by hub card Internal time counter synchronized with IEEE-1588-2008 card
Programmable timing unit for generating specific clock or trigger sequences for sampling
Common synchronized clock
White Rabbit PTP core being developed
Hub card
Notes: Any method using single line for time stamp can be used
IRIG is most well known implementation
Adapted using LVDS signaling
Compatibility for future expansion

## Slide 20: FPGA-based programmable timing module
ATCA-PTSW-AMC4 RTM
Trenz Gigabee Spartan 6 FPGA
10/100/1000 GbE | IEEE-1588-2008 master clock
IRIG-B timing signals | 2 ns synchronization between boards
IEEE-1588-2008 over Ethernet synchronization | ZHAW core
~25 ns RMS time resolution

## Slide 21: ITER prototype Fast Plant System Controller
Controller/PSH
Mini-CODAC & archiving server
ATCA-IO-Processor
ATCA-PTSW-AMC4
HPC
ATCA Shelf
beta version
PCIe
TCN (IEEE-1588)
DAN
SDN
PON
Networks
Hardware

## Slide 22: EPICS interface @ Mini-CODAC
Hardware Monitoring & Settings
System State Machines
High Performance Networks Monitoring
Control & Data Acquisition

## Slide 23: Fault-tolerance benefits system’s availability
Fault-tolerance features automatically mitigate possible failures while still maintaining a stable and satisfactory performance
Redundant resources are managed by the system to establish the desired level of functionality, compensating for eventual failures
Fault-tolerance directly linked with redundancy capabilities

## Slide 24: Redundancy schemes for High Availability
Spare PCIe host stands in for faulty host (“active-standby” 1+1 redundancy)
N+1 redundancy of node boards
N+1 redundancy of AMC cards
Several redundancy schemes can be implemented, supported by ATCA/IPMC
Data assigned to spare units upon fault detection
1
2
3

## Slide 25
Full (2N) (1+1) Redundancy
IPMC
IPMC
IPMC
IPMC
IPMC
IPMC
IPMC
IPMC
IPMC
IPMC
IPMC
IPMC
IPMC
IPMC
Host 1
(active)
Host 2
(standby)
System
manager
Dual-star topology
Redundant hosts
N active + N spares (Active-Standby mode)
In case of failure of hub/node blade the whole standby system takes over
The faulty blade is hot-swapped by a spare, while being repaired
Highest availability scenario
Does not require cable changes on Hot Swap (Full redundant cabling)

## Slide 26: Instrumentation in ITER port cells subjected to high level of radiation (neutrons and g-rays) and high magnetic field
.
Port Cell
105 neutrons/cm2/s @ ~0.1 MeV
102 neutrons/cm2/s @ ~14 MeV
2 mGy/h from g-rays
B = 20-50 mT
Bioshield
1-2 Gy/h from g-rays
1 SEU / min. for fast controller boards corrupt data or system hangs-up
Life time limit of 50 Gy g-exposure for analog COTS
HV power supply failure due to SEB Careful components selection necessary ~1 SEB / 10 hours for COTS PS@ 300 V

## Slide 27: Secluding the controller from radiation areas
RTM with PCIe over Optical Fiber for ATCA PCIe Switch card
One Stop Systems fiber optic PCIe x4 connection kit (10 and 100 m length)

## Slide 28
Secluding the controller from radiation areas
IPFN ATCA demonstration system with hardware and software level Hot Swap exhibited at ANIMMA 2015
100 meter fiber optics link to computer allows host to be located far from risk of hazardous radiation exposure
The platform can be configured for other redundancy schemes (N+M)

## Slide 29: Advanced Methodologies for radiation-tolerant sYSTems AMETHYST
Non radiation hardned COTS products, based on SRAM FPGAs
Minimize radiation immediate effects (SEU) and transient effects
Functional & performance monitoring through system life-cycle to diagnose long- term effects
Implement in high-availability ATCA systems
Perform functional testing on irradiation testing facility
n

## Slide 30: Irradiation Test Facility | RPI @ IST
Fast neutron irradiation facility E4:
Irradiation chamber at the exit of the neutron beam tube;
Prolongation inside the tube;
Neutron and gamma filter;
Periphery of the fission reactor core inside the water cooling/shielding pool.
The neutron fission spectrum at the irradiation facility E4 has a maximum intensity around 2 MeV and a maximum practical energy around 17 MeV. For a 1 MW operation the total neutron flux is 2.74ₓ108 n/cm2/s and decreases linearly with the reactor operating power.
Neutron fission spectrum
Maximum intensity @ 2 MeV
Maximum practical energy @ 17 MeV.
For a 1 MW operation
Total neutron flux 2.74 x 108 n/cm2/s
decreases linearly with reactor operating power

## Slide 31: Irradiation Test Facility | RPI @ IST
Fast neutron irradiation facility E4:
Irradiation chamber at the exit of the neutron beam tube;
Prolongation inside the tube;
Neutron and gamma filter;
Periphery of the fission reactor core inside the water cooling/shielding pool.
The neutron fission spectrum at the irradiation facility E4 has a maximum intensity around 2 MeV and a maximum practical energy around 17 MeV. For a 1 MW operation the total neutron flux is 2.74ₓ108 n/cm2/s and decreases linearly with the reactor operating power.

## Slide 32: Virtex 6 irradiation results and conclusions
FPGA irradiation test with
SEM controller and BRAM sensor performing real-time SEU detection-correction, using Error Correction Code (ECC) for repairing SEU bit-flips in the Block RAM and configuration memories
FPGA clocks stopped performing only BRAM and configuration read-back afterwards
Detected SEU increase linearly with reactor power
SEU detected by the SEM controller are higher than SEU detected by BRAM sensors, since the configuration memory is larger relatively to BRAM
For irradiation fluxes higher than the fluxes for ITER port cells the number of unrecoverable errors was low
SEU detection and mitigation techniques can increase the reliability and availability of FPGAs used in ITER port cells
Notes: O IP core da Xilinx, o SEM, monitoriza a memória de configuração, mas a reparação dos bit-flips nessa memória pode obrigar a reconfigurar a FPGA, portanto a expressão “tempo real” para a memória de configuração pode ser um pouco ambígua. O tempo de reprogramar a memória de configuração (ms) pode ser excessivo, relativamente ao tempo disponível para o controlador actuar correctamente. Os sensores de BRAM detectam muito mais rapidamente a ocorrência de SEU, e os BRAMs com ECC podem corrigir os valores lógicos incorrectos, daí a vantagem de monitorizar os blocos de memória associados à lógica que implementa a funcionalidade. Sobretudo quando se verificar uma rápida variação da intensidade de radiação do reactor (com a correspondente rápida variação de incidência de SEUs), a rapidez com que os sensores BRAM detectam essa variação pode ser uma vantagem decisiva na activação de mecanismos de aumento de robustez do controlador.

## Slide 33: Roadmap for ATCA HA systems
Sampling rate
Channel Density
AMC* 1-3 GSPS
* Under development
ADC MIMO *
AMC* 100 MSPS+
10 MSPS, 16 bit
6 MSPS
Magnetics Soft X-rays
Bolometry
ECRH monitoring
…
Plasma Position Reflectometry
Thomson Scattering
Low Level RF (ESS-B)
ITER Radial Neutron Camera
…
X-rays | PHA
G-ray spectroscopy
Neutron spectroscopy
…
PCIe over optical fiber | RTM
Timing | White Rabbit

## Slide 34: Fast digitizer | AMC and FMC cards
AMC-MKX1, a single-width, full size AMC card
Processing capability: Xilinx® KintexTM 7 (XC7K325T);
AMC Storage capability: 2 GB of DDR3 SDRAM, 128 MB DDR3 ;
AMC PCIe protocol: 1 PCIe Endpoint (4 PCIe 2.0) ;
Hardware Management: Module Management Controller (MMC);
Standards Compliance: Suitable for ATCA and ATCA platforms;
I/O expansion : High-pin-count VITA 57 (FPGA Mezzanine Card (FMC) site);
Applications: Demanding physic experiments with high-performance processing needs (eg. Nuclear Fusion);
FMC-AD-1Gx, full-size FMC digitizer module
Dual-channel ultra-high speed analog-to-digital converter up to
3.2 GSPS @ 12 bits; or
Single-channel sampling rate up to 1.6 GSPS @ 12 bits;
AC or DC coupling;
180.60  73.50 mm
83  69 mm

## Slide 35: High availability research programe | Key pillars
ongoing
  MIMO system | high channel density
  High-availability for long operation | very reduced downtime
  Serviceability | Remote hardware management, hot-swap, modularity
  Integration into CODAC | HMI, alarm handlers, databases
  Timing and Event management
  Modularity / Expandability
  High performance & Computational power | Real-time complex algorithms
  Redundancy | sensor level, system level, software/firmware level
  Fault detection and mitigation
  Resilience to errors
  Resilience to neutrons | Single Event Upsets
  Resilience to magnetic fields
  COTS availability
These activities are ITER-relevant (but also for other experiments), urgent & scientifically interesting
Notes: (per channel/groups of channel)
On the next slides I’l present some of the thcnical solution solutions chosen in the engeneering phasee

## Slide 36: IPFN ATCA dissemination
ISTTOK
ESS-B
JET
W7-X
COMPASS
RFX
ITER
TCA-Br
CERN
xTCA interest Group
Implemented /ongoing
Discussion / Pending
ASDEX-Up