## Slide 1: Optical fibre test update
P8 test installation
Rainer Schwemmer 9.4.2015

## Slide 2: Setup
Review of TDR suggested a test installation at P8 to ensure the viability of the long distance read-out
Installed 3 Trunk cables with 144 fibers each from different providers at P8
  1 x 144 Fibers from Fibernet, pre-connectorized
  1 x 144 Fibers from CERN, pre-connectorized
  1 x 144 Fibers from CERN, spliced
All 432 Fibers have been tested and have expected Attenuation
Currently Measuring the spliced fibers
  Worst case scenario due to additional attenuation of splice point
Testing on loop with 2 x 350m
  Higher attenuation than in final setup
  AMC40 transmitter has more optical power though
  Longer fiber just about compensates for the stronger transmitter
2
AMC40
Patch Panel
SX8
(Gas Building)
Patch Panel
UX8
Bunker
BER tester
~ 350 m

## Slide 3: Result so far
Setup has been running for approx. 65 days now
3.27x1017 bits tested so far
0 Errors
However BER < 1 / 3.27x1017 only with 63% confidence
3
CL = Confidence Level
N = Number of bits tested
E = Errors
BERs = Specific Error Rate
Confidence | 63% | 74% | 95%
Aggregated BER | < 3.1 x 10-18 | < 4 x 10-18 | < 9 x 10-18
Error rate for 12k fibers | < 16 / day | < 20 / day | < 45 / day

## Slide 4: Outlook
At the current rate we need to test for 2925 more days to ensure < 1 error per day (2x10-19) with 95% confidence
If we used all installed links we needed 82 more days
  Would need 11 more AMC40s though
What is an acceptable error rate?
Bit Errors in Data only contribute to noise
Bit Errors in Headers  De-synchronization
  TODO: What is the estimated rate for this happening and is it acceptable?
4