## Slide 1
East Area Consolidation
Konstantinos Papastergiou
CERN Technology Department | Electrical Power Converters
With information by J-L. Blanc, G. Le Godec, J. Cottet and J-P Burnet
01 April 2015

## Slide 2: Previously discussed
The East Area Energy Consumption is high at 15GWh/yr
  Third highest consumer after PS (55GWh) and PS Booster (25GWh)
  Continuously energised BUT used < 4% of time for physics operations
  DC powering of magnets  unnecessary cooling requirements
Cycling the magnet current can save electricity
  Energy requirement from 11GWh to 0.6GWh per year
  Saving estimated at 600kCHF per year* for new EA configuration
Example of a self-funded project
  Extra cost originally estimated 3MCHF (Magnets+P. Conversion)
  Short investment depreciation time - approximately 5 years
New technology is being developed for transfer lines
* Source: J.Cottet, Energy Balance of the East Area and possible Improvements, 2012

## Slide 3: 2012 proposal

## Slide 4: Cycling magnet operation
Cycling operation requires a di/dt through the magnet
  23/55 magnets do not support cycling due to a solid steel yoke
  Eddy currents would heat up the yoke material

## Slide 5: Energy Consumption: detail
5
84%
12%
4%
Equipment | Energy in MWh
T8 Spectrometer | 6 360
T7 Spectrometer | NA
Building 251 | 5 386
SMH 57 AND 61 | 22
Building 263 | 1 303

## Slide 6: Magnet refurbishment cost
Type | Estimated Price magnet (kCHF) | Number of magnets | Total cost per family (kCHF)
MDX | 20 | 6 | 120
M100 | 70 | 2 | 140
M200 | 100 | 5 | 500
Q100 | 50 | 5 | 250
Q200 | 70 | 4 | 280
Q74 | 40 | 1 | 40
Total |  | 23 | 1.3 MCHF
Solution Elaborated by the Magnet Groups at CERN
replacement all the solid steel yokes by new laminated yokes while keeping the present coils
Total magnet refurbishment cost is 1.3MCHF
Considerable cost – could it be financed by energy saving?

## Slide 7: Pulsed Operation: consumption
FUTURE OPERATION (HYPOTHESIS) |  |  | 
Zone | number of cycle per Supercycle | duration in 2011 (in hr) | duty cycle
Total - East | 6 | 4301 | 15%
EASTA | 2 | 4301 | 5%
EASTA on T9 | 1 | 4301 | 2.5%
EASTA on T10 | 1 | 4301 | 2.5%
EASTB | 4 | 4044 | 10%
CALCULATION RESULTS: ENERGY-WATER CONSUMPTION |  |  |  | 
 | Pulsed Mode |  | Continuous Mode | 
 | Energy in MWh | Price in kCHF | Energy in MWh | Price in kCHF
Total magnet electrical consumption | 557 | 28.3 | 9 128 | 464
Water cooling electrical consumption | 79 | 4.0 | 1 294 | 66
Air cooling electrical consumption | 26 | 1.3 | 431 | 22
Total electricity consumption | 662 | 33.7 | 10 853 | 551.8
Total cooling fluid cost |  | 6.2 |  | 101.5
TOTAL energy cost |  | 40 kCHF  |  | 653 kCHF 

## Slide 8: Direct versus Cycling operation
Magnet type | Total (1.2sec) | Recoverable | Thermal loss (1.2sec)
Quadrupole (26Gev) | 11kJ | 6kJ | 5kJ
Small Dipole (26Gev) | 31.5kJ | 25kJ | 6.5kJ
Large Dipole (26Gev) | 101kJ | 82kJ | 19kJ
* Assuming cost of electricity between 0.05 and 0.065CHF/kWh. 1kJ of energy over a 1.2sec cycle corresponds to 1kJ/1.2sec=0.83kW of average power. Assuming this 1.2sec (PS) cycle repeats for 24hours over 270 working days the total energy required from the power network (for each 1kJ) is 5378kWh/annum. If this energy is not recovered in capacitor banks after every magnet cycle it is returned to the power network and is not remunerated by the provider.
Annual cost of electricity for 1kJ:
(Non-recoverable/consumed every 1.2seconds)
270-350 CHF*

## Slide 9: The System View
From DC to Cycling magnet current:
Reduction of power converter RMS rating by 40-45%
Reduction of power losses in magnets
Reduction of cooling requirements

## Slide 10: Magnet Energy Recovery
Magnet Energy Recovery is a specific variant of power cycling in which energy is stored locally in the power converter instead of returning it to the grid

## Slide 11: System Level Gains
(Cost: ~225CHF/kJ)
Benefits of energy recovery in the converter:
Significantly lower costs of grid interconnection equipment
Grid infrastructure standardisation/standard equipment
Lower capacity of reactive power compensation
Fault ride-through capability of power converters

## Slide 12: Examples of converter standard bricks

## Slide 13: Cycling Operation Impact
Cycling operation will raise the project costs:
  Magnet consolidation of solid steel yokes: 1.3MCHF
  Power Converter replacement costs will increase > 1.5MCHF (to 3M+)
    Power converter consolidation was already scheduled
  Electrical distribution costs will be lower
    2x2MVA transformers are sufficient to power the EAST Area (currently 8 transformers)
And will result recurring savings:
  Up to 10GWh/year
  Up to 600kCHF/year
…and a much smaller carbon footprint from the East Experimental Area
Depending on the level of consolidation desired the project additional costs be recovered in 5-10 years of operation (~4500h/yr)
preliminary
figures

## Slide 14: Magnet Map
110kCHF
12kCHF/yr*
* Accounting for magnet losses only
preliminary
figures

## Slide 15: Introduce to key figures
Key cost drivers of the project (in the following order)
  8xMCB (800Apk) (204kJ per circuit)
  4xM200SP (750Apk) (274kJ per circuit)
  2xM100SP (600Apk) (119kJ per circuit)
Converters with local energy recovery or mix of technologies?
Multiple or single scenario for P.Conversion budget?

## Slide 16: Related documents
G.Le Godec, Energy Recovery and Modular Approach: introduction to a collaboration, TETM, CERN (EDMS 1295364)
J.Cottet, J-P.Burnet, Energy balance of the East Area and possible improvements, TETM, CERN
S.Rossini, K.Papastergiou, Magnet Energy Recovery: a review of topologies and energy management strategies, 2014, EDMS1450551
D.Tommasini, Practical definitions and formulae for magnets, CERN, Geneva (EDMS1162401)
K.Papastergiou, Functional Specification: Economy Mode Operation in Accelerator Transfer Lines, EDMS1493325



