## Slide 1: HL-LHC integration Focussing on underground infrastructure Baseline frozen on the 18th/09/2015
INTEGRATION: C. Magnier, S. Maridor, B. Vazquez de Prada
R. Calaga, F. Killing, E. Montesinos and the whole WP4
A. Masi, A. Rossi, S. Redaelli and the whole WP5
A. Ballarino, A. Jacquemod and the whole WP6a
J.P. Burnet, C. Coupat and the whole WP6b
F. Rodriguez Mateos, D. Wollmann WP7
S. Claudet WP9
G. Arduini, M. Fitterer: WP2
EN-MME: M. Guinchard Lukasz Jerzy Lacny
WP17: Isabel Bejar Alonso
R. Calaga, F. Killing, E. Montesinos and the whole WP4
J.P. Burnet, C. Coupat and the whole WP6b
S. Claudet WP9
EN-EL: Gerard Cumer, Nuno Dos Santos, Jean-Claude Guillaume
EN-CV: M. Battistin, F. Boralho, P. Pepinster
EN-HE: C. Bertone, B. Feral, R. Rinaldesi, I. Ruehl
GS-ASE: T. Hakulinen, S. De Luca, P. Ninin
GS-SE: J. Osborne, P. Mattelaer
T. Otto
DGS-RP: C. Adorisio
DGS-SEE: J. Gascon
And many others
Prepared by P. Fessia

## Slide 2: Summary
The vibration issue
The Double Decker approach in a nutshell
What we need to fit in the Double Decker
Optimising: reasons, consequences, timing and first actions in list (my optimistic approach)
Conclusions

## Slide 3: The vibration issue

## Slide 4: Issue: vibrations induced by Civil Engineering excavation equipment possibly perturbing LHC exploitation

## Slide 5: Effect of vibrations on the beam
  Effect of construction works next to IR1/5:
    main effect is a closed orbit distortion due to displacement of quadrupoles
    long term (weeks) drifts could be compensated with orbit correctors or more frequent alignment campaigns
    short term drifts (minutes/hours) could be compensated by current orbit feedback
    low frequency vibrations can not be compensated by current orbit feedback
      largest contribution is expected from the inner triplet during collision due to high β-function and strength
      main effects:
        luminosity loss due to separation of the beams
        increased losses at collimators (Run I: around 40 μm orbit deviation at TCPs caused high losses)
        emittance growth/increased halo diffusion rate -> luminosity loss and higher losses at collimators
      closed orbit distortion depends on wavelength of the vibrations, e.g. ±1 μm displacement of the IT can result in 0-14 μm separation of the beams at the IP and 3-170 μm residual orbit at collimators (1)
    Possible mitigation measures: warm magnets for low frequency
    (0-200 Hz) closed orbit feedback system in IR1/5
    (1) Run III parameters: Nbunch=1.25x1011, εN=2.0 μm, Ntot=2740, β*(IP1/5)=0.4 m (option med RunII), E=6.5 TeV, σIP=10.7 μm
G. Arduini,
M. Fitterer
Notes: Q=tune, not the fractional tune!

## Slide 6: Which are the ingredients of the problem ?
    Build the transfer function from the point where the excavation takes place to the beam axis
In (ω)
Out (ω)
H1 (ω)
H0 (ω)
H0 (ω)
H1 (ω)
Beam stability
1μm

## Slide 7: Results about H0 (ω)
H0 (ω)
Vertical
Transversal
Displacement with hammer impact
Ampl. factor with CE activity
8Hz
Rigid movement on feet
24 Hz
First bending mode
Courtesy M. Guinchard,
Lukasz Jerzy Lacny

## Slide 8
Tunnel transfer function H1 (ω) estimation
Positions :
+25 m, +10m, 0 m , - 10 m
80 m

## Slide 9
25R
10R
0
10L
Chart: Frequency [Hz]
| 2 | 3 | 5 | 8 | 12 | 18 | 24 | 28 | 35 | 42 | 49 | 60 | 70 | 85 | 98 | 127 | 148 | 174 | 198
G 0/0R | 0.032573 | 0.033168 | 0.029728 | 0.030364 | 0.021413 | 0.010286 | 0.013943 | 0.019509 | 0.019833 | 0.020159 | 0.020231 | 0.009337 | 0.01104 | 0.014762
G 10L/0R | 0.033628 | 0.032674 | 0.029664 | 0.033066 | 0.022531 | 0.01118 | 0.012756 | 0.016939 | 0.021559 | 0.019002 | 0.019013 | 0.009366 | 0.009631 | 0.011004
G 10R/0R | 0.031993 | 0.024835 | 0.026759 | 0.03065 | 0.02023 | 0.01104 | 0.010911 | 0.016181 | 0.01985 | 0.019417 | 0.014052 | 0.010835 | 0.010567 | 0.015562
G 25R/0R | 0.028751 | 0.025887 | 0.024507 | 0.02795 | 0.019945 | 0.007532 | 0.011978 | 0.016108 | 0.017647 | 0.016618 | 0.005232 | 0.006847 | 0.006461 | 0.010399
S 3/1 | 0.065421 | 0.05447 | 0.038369 | 0.015026 | 0.017019 | 0.022562 | 0.023419 | 0.019398 | 0.011614 | 0.043531 | 0.027117 | 0.025873 | 0.020457 | 0.013232 | 0.010864 | 0.0083812
S 4/1 | 0.051267 | 0.05888 | 0.035265 | 0.018604 | 0.01751 | 0.024897 | 0.024194 | 0.019351 | 0.011015 | 0.042953 | 0.025622 | 0.024891 | 0.016772 | 0.0089239 | 0.0016253 | 0.0052979
S 3/2 | 0.048077 | 0.039839 | 0.028785 | 0.011651 | 0.012678 | 0.016762 | 0.022714 | 0.019872 | 0.026538 | 0.013518 | 0.014762 | 0.016677 | 0.019404 | 0.031965 | 0.0062514 | 0.0026709
S 4/2 | 0.037675 | 0.043064 | 0.026456 | 0.014426 | 0.013043 | 0.018497 | 0.023466 | 0.019823 | 0.02517 | 0.013339 | 0.013948 | 0.016044 | 0.015909 | 0.021558 | 0.00097175 | 0.0016884
Courtesy M. Guinchard,
Lukasz Jerzy Lacny
Chart: Frequency [Hz]
| 2 | 3 | 5 | 8 | 12 | 18 | 24 | 28 | 35 | 42 | 49 | 60 | 70 | 85 | 98 | 127 | 148 | 174 | 198
G 10L/0 m | -1.34 | -0.41 | -2.54 | -1.92 | -1.88 | -4.79 | -7.81 | -5.36 | -10.28 | -15 | -7.71 | -20.06 | -20.43 | -21.08
G 10R/0 m | 0.62 | -6.66 | -15.98 | -15.1 | -25.78 | -20.92 | -33.31 | -38.82 | -50.81 | -60.35 | -48.73 | -74.63 | -88.08 | -107.39
G 25R/0 m | -9.41 | -17.98 | -36.63 | -32.16 | -62.03 | -61.37 | -68.78 | -101.28 | -125.74 | -141.49 | -114.37 | -177.29 | -223.21 | -255.88

## Slide 10: Putting the pieces together
In (ω)
Out (ω)
H1 (ω)
H0 (ω)
Chart: Frequency [Hz]
| 2 | 3 | 5 | 8 | 12 | 18 | 24 | 28 | 35 | 42 | 49 | 60 | 70 | 85 | 98 | 127 | 148 | 174 | 198
G 0/0R | 0.032573 | 0.033168 | 0.029728 | 0.030364 | 0.021413 | 0.010286 | 0.013943 | 0.019509 | 0.019833 | 0.020159 | 0.020231 | 0.009337 | 0.01104 | 0.014762
G 10L/0R | 0.033628 | 0.032674 | 0.029664 | 0.033066 | 0.022531 | 0.01118 | 0.012756 | 0.016939 | 0.021559 | 0.019002 | 0.019013 | 0.009366 | 0.009631 | 0.011004
G 10R/0R | 0.031993 | 0.024835 | 0.026759 | 0.03065 | 0.02023 | 0.01104 | 0.010911 | 0.016181 | 0.01985 | 0.019417 | 0.014052 | 0.010835 | 0.010567 | 0.015562
G 25R/0R | 0.028751 | 0.025887 | 0.024507 | 0.02795 | 0.019945 | 0.007532 | 0.011978 | 0.016108 | 0.017647 | 0.016618 | 0.005232 | 0.006847 | 0.006461 | 0.010399
S 3/1 | 0.065421 | 0.05447 | 0.038369 | 0.015026 | 0.017019 | 0.022562 | 0.023419 | 0.019398 | 0.011614 | 0.043531 | 0.027117 | 0.025873 | 0.020457 | 0.013232 | 0.010864 | 0.0083812
S 4/1 | 0.051267 | 0.05888 | 0.035265 | 0.018604 | 0.01751 | 0.024897 | 0.024194 | 0.019351 | 0.011015 | 0.042953 | 0.025622 | 0.024891 | 0.016772 | 0.0089239 | 0.0016253 | 0.0052979
S 3/2 | 0.048077 | 0.039839 | 0.028785 | 0.011651 | 0.012678 | 0.016762 | 0.022714 | 0.019872 | 0.026538 | 0.013518 | 0.014762 | 0.016677 | 0.019404 | 0.031965 | 0.0062514 | 0.0026709
S 4/2 | 0.037675 | 0.043064 | 0.026456 | 0.014426 | 0.013043 | 0.018497 | 0.023466 | 0.019823 | 0.02517 | 0.013339 | 0.013948 | 0.016044 | 0.015909 | 0.021558 | 0.00097175 | 0.0016884
Chart: Frequency [Hz]

## Slide 11: Measurements
  Are the IT eigen-frequencies visible in the LHC beam spectrum?
  Principle: β-function during squeeze changes mainly in the IT in IR1/5 -> IT eigen-frequencies are visible in the beam spectrum if an increase of the amplitude for the IT eigen-frequencies is observed during the squeeze
  Result: 20 Hz first vertical eigen-frequency visible, 10 Hz peak visible, but no increase of amplitude during squeeze
G. Arduini,
M. Fitterer
  MD to study effect of a low frequency noise on emittance evolution and tail population
  beam and machine setup:
    weak-strong scenario (single bunch) at injection (colliding)
    mimic long-range encounters with octupoles
    apply sinusoidal (10 Hz horizontal, 20 Hz vertical) excitation on both beams
  record time evolution of emittance + tail population with wire scanners and BSRT and diffusion rates with collimator scans

## Slide 12: Conclusions and consequences
No margin to perform CE engineering work during LHC beam operation (we need factor 10 and it could be that we see already signature today of the cultural noise)
Today the only viable way is to perform work out of beam time that means anticipating to LS2
SH
AFT
Caverns and tunnel
F
I
N
I
S
H
I
N
G
C
O
N
N
E
C
T
I
O
N

## Slide 13: The Double Decker in a nutshell

## Slide 14: Double decker key facts
Allows having the underground infrastructure on the same side of the LHC tunnel both for Point 1 and Point 5 (avoiding interference with the transport area)
Reduce the depth of the pit (≈ -11 m)
Provide solution to bring much nearer RF equipment to the RF crab cavities and to access the DFX and DFM from a convenient angle with the SC link. It eases the installation of the SC links and its integration (SC links get also shorter about 60 m).
Reduces the disruption in LS3 of the LHC tunnels with benefit from the planning point of view, avoiding to transport the gravels out from the experimental pits and reducing the risk of inducing structural problem to the LHC machine tunnel
Increase the distance between the LHC machine and the UR/US providing good radiation shielding, limiting naturally ODH risk from the LHC main tunnel, allowing access during operation and increasing further vibration reduction during excavation ( Shaft moved far from the IT area)
Provide the solution for the connection to the BBLRs , if they will be integrated in the baseline (space already accounted for)
It is considered that the following equipment can be installed in the LHC tunnel
  Q.H. power units: possible location present installation area for the IT power converters
  Extra collimation racks near the present collimation racks
Key requirement:
access to all the active equipment installed in the underground structure in all the machine conditions included in beam

## Slide 15: Double Decker safety
All required ventilation and safety ducts have been added as such for this integration. The real related loads should be re-analysed in the next optimisation phase
Emergency rooms have been installed along the tunnel length
A safety exit from the UA opposite to the main access shaft to the LHC tunnel is under study (not pictured here). The implementation requires in depth analysis of the impact of linking the LHC tunnel and the Double Decker structure (importing risks, operational impact,…). Its addition it is transparent from the integration point of view with the exception of ventilation and accesses.

## Slide 16
Triggering
The 1.9 K Cold Box output shall not be 18 meters higher than the distribution line ->
use this constraint as an opportunity to:
Increase the distance between the service tunnel and the machine
(vibrations and radiation attenuation)
Avoid to invade the transport area
Provide smarter access for the connection between cryo and powering to the machine
Reduce the impact on the LS3 decoupling the planning as much as possible
Provide opportunity for system optimisation for efficiency and costs
Target technical infrastructure installation during Run III
The Double Decker approach
C
R
A
B
Powering
and
protection
1.9 K cold box and cryogenic distribution lines start
QXLs
SC LINKs
Q1 to D1

## Slide 18: What we need to fit in the Double Decker?

## Slide 19: The Shaft (PM): how to fill 12 meter of diameter
Vertical transport
area
4mx8m
[CE] Concrete module
[CE] Metallic module
Services and stairs
[HE] LIft 3t
Safety stairs
[CV] Injection fresh air
Ø950mm
[CV] Extraction for batteries
Ø250mm
[SU] access to
reference point
Ø100mm
[SU] access to
reference point
DN 100mm
[CV] water I/O
DN 300mm
[CV] Pumping drain water
DN 100mm
[CV] Pressurisation sas
Ø750mm
[CV] Smoke extraction
UR+UA+UL
750x750mm
[CV] Smoke extraction
US
750x750mm
[EL] Safety cables
[CRG] cryogenic connection
Surface underground
1m2
[IT/CS]
2 cables for GSM
[EL]
2x8 cable trays
[CV] Cold water I/O
DN 150mm
[CRG] QURCG
PM
[CE] PM-Ø12m

## Slide 20
RF for crab right side
CV
CRG
US part I:
PM lowering volume, concrete pressurized volume and lift, safe room, 1.9 K Cold Box with cryogenic distribution lines, transformers and low voltage departures

## Slide 21
PM metallic support structure for services and stairs
Metallic structure to support floor 1
Floor in the CRG area : + 3.8m
False floor for cabling everywhere else (except UW) : +4.3m
Loading access to 1st floor
US Part II:
Metallic support structures for equipment, personnel and services

## Slide 22
RF (and BBLR) Faraday cage
Right side
US part III:
Faraday Cage for the RF and for the BBLR

## Slide 23
Other Racks :
Access system : x5 (it could go to surface)
Survey : x 1
RF
SSA : x 6
PLC : x 4
Not assigned spare racks : x 7
Cable trays
US Part IV:
Racks, control and cable trays ….
Cryogenic electrical supply and controls
2 x (6000 mm x 600 mm x 2200 mm)
1 x (4000 mm x 600 mm x 2200 mm)
1 standard rack

## Slide 24
Air treatment units
US Part V:
UW with the CV units

## Slide 25
General view with all the cooling and ventilation distribution

## Slide 26
Point 1
Overall view: US, UW, URs, UAs and ULs

## Slide 27
RF ZONE
The UA dedicated to RF installation
Crab cavity

## Slide 28
Geometry 4.4
UA: the Radio Protection studies: implemented geometry
LHC tunnel
~162 from IP
RF service gallery - UA
Power converter gallery - UR
RF service gallery - UA
RF service gallery - UA
RF service gallery - UA
Connection cores
LHC tunnel
~162 from IP
LHC tunnel
~162 from IP
Courtesy C. Adorisio

## Slide 29
Effective Dose Profile (accidental scenario)
Accessible
Area set at 1 mSv
6 mSv
Accidental max allowed exposure
UA tunnel start
13 m
Effective Dose (mSv)
X (cm)
Courtesy C. Adorisio
This position matches the 0.2 µSv/h in operation.
Limit for Non-Designated area < 0.5 µSv/h

## Slide 30
tetrodes
circulator
Coax cables
EQUIPEMENT RF
OPTION : TETRODE
Integration with Tetrode Option.
Remark: IOT option requires less volume underground, but a building on surface. The Integration account for the envelope of the two

## Slide 31
BBLR :
Powering 2* 8 RACKS (UR)
Control 2*4 RACKS (UR/US) Faraday cage
CAGE DE FARADAY
RF and BBLR

## Slide 32
SC Magnet Powering I: D2 to Q6

## Slide 33
SC Magnet Powering II: Q1 to D1

## Slide 34: Electrical supplies
Transformers for PC for magnets
Transformer and distribution RF LEFT SIDE

## Slide 35
Unit for the powering warm cables
Unit for UA
2.5 m x *2.5 m x 7 m
2 x (2.3 m x 2.3 m X 8 m)
6 x (1.5 m x 1.5 m x 3.5 m)
Ventilation
Units for local air treatment

## Slide 36
2*DN 300 (PC)
2*DN 150 (AHU)
2*DN 200 (RF_UA13)
RIA
Signal (Transit RF, Access, …)
High Voltage
General services
SAFETY
AC distribution
Signal (local)
Opt. Fibres + IT
RF HV cables
SMOKE EXTRACTION (750*750)
COOLING FOR WARM CABLES
QXL_L
QXL_R
PULSION FRESH AIR (Ø800)
He return line
The most busy section with all longitudinal services

## Slide 37: Optimising reasons, consequences, timing and first actions in list (my optimistic approach)

## Slide 38: One of the reasons to optimise: volume to excavate
1 – OLD BASELINE :
2 - OPTION :
≈ 20 000 m3
≈ 28 000 m3
CS review
CE optimisation and
D. Decker approval
≈ 33 000 m3
≈ 41 000 m3
Volume integration completed

## Slide 39: Optimisation for cost efficiency targeting possible reduction of infrastructure needs
In beam machine equipment requirements
Machine equipment services
Cooling and ventilation supply
Electrical supply
Civil engineering
design

## Slide 40: Shaft
TARGET:
Reduction of diameter of the shaft from 12 m
BENEFITS:
Reduction of CE cost
Reduction of excavation time->planning risk mitigation
Reduction of the water infiltration risks and volumes at Point 5
MEANS/ISSUES TO DEAL WITH
Need to transport the QURC in inclined or vertical position
Provide sufficiently and correctly positioned routing for ventilation and cable trays
From 12 to 10 m:
Model under screening and study

## Slide 41: UR
TARGET:
Reduce the ohmic heating of the SC magnet powering installation without increasing the cold part length
BENEFITS:
Reduction of the warm and water cool cable footprint
Reduction of the ohmic dissipation
Reduction of the electrical installation footprint
Reduction of the cooling ventilation system
Reduction of the UR diameter (to be seen)
Reduction of capital and operative cost
MEANS/ISSUES/OPTIONS/OPPORTUNITIES TO DEAL WITH
Adoption of 2 quadrant PCs for the Q1->Q3 circuit
Adoption of 2 quadrant PCs for the D1 and D2
Allowing to place PCs as near as possible to the DFHs in electrical dissipation reduction approach
Dropping of the Dump and Switches for Q1->Q3 circuit
Lumping of Q1->Q3 in one circuit

## Slide 42
Optimisation working hypothesis

## Slide 43
-40%
-40%
-40%

## Slide 44: UA
TARGET:
Reduce the ventilation installation and if possible reduce the UA diameter
BENEFITS:
Adopt similar strategies for the RF crab powering baseline (tetrodes) and IOT powering with the HVPS in surface on both cases
Reduce the powering delivered to the air in the UA
MEANS/ISSUES/OPTIONS TO DEAL WITH
Installation of the HVPS for the tetrodes on the surface

## Slide 45: Timeline
Phase I: COMPLETED
Definition of the full needs and full integration in tunnel and first analysiss on surface: USED FOR THE INVITATION TO TENDER FOR THE CIVIL ENGINEERING DESIGN
Phase II: ONGOING
Optimisations of volumes and of the technical Infrastructure Specification (WP17). It will provide refine drawings for the SIGNATURE OF THE CIVIL ENGINEERING DESIGN. February 2016
Phase III: continuous improvement and refinement keeping in line the milestones for civil engineering activities
Double decker it is taking up speed, we can steer, but better do not break or it will be painful for passengers

## Slide 46: Conclusions
The approach for the installation of the supplies and services for the HL-LHC has been reviewed following the vibration studies
The Double Decker approach has been developed and, on the base of this approach, all the services identified by WP17 integrated
The volumes for the surface (not shown here) and underground infrastructures have been frozen as first complete Baseline on the 18th/09/2015

## Slide 47: Extra slides

## Slide 48
Type 2: 13 kA
Type 3: 6 kA
Type 4: 2kA
4 * Type 7(0.12kA)= 1 racks
2 * Type 5(0.3kA) = 1 racks
2 * Type 6(0.2kA) = 1 racks
Type 1: 16.5kA
≈12 m2
“switch”
dump
Location | Quench Detection Systems (QDS) | PIC | WIC/ FMCM | BIS | CLIQ
 | # of Racks | # of Racks | # of Racks | # of Racks | # of Racks
L1 | 8 | 2 | 1 | 1 | 22

## Slide 49
2* 4 RACKS (UR)
2*1 RACKS (UA13/17)
Survey

## Slide 50
PM57
US57
UW57
General View

## Slide 51: Civil engineering structure related to personnel safety
PM57
US57
UW57
Pressurised safety area
Leak tight pressurised concrete module

## Slide 52
PM57
US57
UW57
Vertical lowering volume 4 m x 8 m.
50 cm margin on sides for largest element
Transport volume in the shaft

## Slide 53
Overhead crane
5t for cold box maintenance
US handling equipment ( more foreseen in the UW)

## Slide 54
QURCG
QXLR & QXLL
QPLG
Cryogenic installation without control and electrical supply part

## Slide 55
Safe room
Safe room

## Slide 56
Cooling water treatment
and circulation
UW ground floor

## Slide 57
UR
UA
Transport area ground floor
UA
UR
Ground floor with transport areas

## Slide 58
Ventilation Distribution
General view with all the cooling and ventilation distribution

## Slide 59
First floor
First floor with transport areas

## Slide 60
PM57
US57
UA57
UR57
UW57
General view

## Slide 61
HVPS : 4 RACKS/TETRODE
Integration with Tetrode Option.

## Slide 62: The longitudinal services in the section
2*DN 300 (PC)
2*DN 150 (AHU)
2*DN 200 (RF_UA13)
RIA
Signal (Transit RF, Access, …)
High Voltage
General services
Safety
AC distribution
Signal (local)
Opt. Fibres + IT
RF HV cables
SMOKE EXTRACTION(750*750)
Cooling for the warm cables
QXL_L
QXL_R
PULSION fresh air (Ø800)
He Return lines

## Slide 63
SC Magnet Powering 3D

## Slide 67
VOLUME DE RESERVATION POUR DFH (DFHM ET DFHX)
30 M2
4 RACKS

## Slide 68
(EXTRACT FROM Power_converter_list_V16.xlsx)
POWER CONVERTOR LIST (PC)
SMARTEAM | TYPE | QTY | COMMENTAIRE |  |  | total | 
ST0686322_01 | TYPE 1 | 4 | ENSEMBLE equivalent de | 10 | RACKS | 40 | RACKS
ST0686345_01 | TYPE 2 | 4 | ENSEMBLE equivalent de | 9 | RACKS | 36 | RACKS
ST0049908_01 | TYPE 3 | 8 | ENSEMBLE equivalent de | 6 | RACKS | 48 | RACKS
ST0686309_01 | TYPE 4 | 30 | ENSEMBLE equivalent de | 3 | RACKS | 90 | RACKS
ST0186528_01 | TYPE 5 | 2 | RACKS |  |  | 2 | RACKS
ST0619391_01 | TYPE 6 | 8 | RACKS |  |  | 8 | RACKS
ST0186602_01 | TYPE 7 | 6 | RACKS |  |  | 6 | RACKS
 |  |  |  |  | total | 230 | RACKS
3d
PC type |  | DFHM_L | DFHX_L | IP_L | IP | IP_R | DFHX_R | DFHM_R | Number of rack 19'' BY TYPE |  | RACK BY IP SIDE | TOTAL BY IP
New | Type 1 | 0 | 2 | 2 | 4 | 2 | 2 | 0 | 10 |  | 20 | 40
Existing | Type 2 | 1 | 1 | 2 | 4 | 2 | 1 | 1 | 9 |  | 18 | 36
Existing | Type 3 | 6 | 0 | 6 | 12 | 6 | 0 | 6 | 4 |  | 24 | 48
New | Type 4 | 8 | 7 | 15 | 30 | 15 | 7 | 8 | 3 |  | 45 | 90
Existing | Type 5 | 0 | 1 | 1 | 2 | 1 | 1 | 0 | 0.5 |  | 1 | 2
New | Type 6 | 0 | 7 | 7 | 14 | 7 | 7 | 0 | 0.5 |  | 4 | 8
Existing | Type 7 | 8 | 2 | 10 | 20 | 10 | 2 | 8 | 0.25 |  | 3 | 6
 |  |  |  |  |  |  |  |  |  |  | 115 | 230

## Slide 69
Type 2: 13 kA
Type 3: 6 kA
Type 4: 2kA
4 * Type 7(0.12kA)=
1 racks
2 * Type 5(0.3kA) =
1 racks
2 * Type 6(0.2kA) =
1 racks
Type 1: 16.5kA

## Slide 70
Type 2: 13 kA
Type 3: 6 kA
Type 4: 2kA
4 * Type 7(0.12kA)= 1 racks
2 * Type 5(0.3kA) = 1 racks
2 * Type 6(0.2kA) = 1 racks
Type 1: 16.5kA
≈12 m2
“switch”
dump
Location | Quench Detection Systems (QDS) | PIC | WIC/ FMCM | BIS | CLIQ
 | # of Racks | # of Racks | # of Racks | # of Racks | # of Racks
L1 | 8 | 2 | 1 | 1 | 22

## Slide 71
ENERGY EXTRACTION
≈12 m2
Corrector circuit
“switch”
dump
1 rack = 600 x 900

## Slide 72
Location | Quench Detection Systems (QDS) | PIC | WIC/ FMCM | BIS | CLIQ
 | # of Racks | # of Racks | # of Racks | # of Racks | # of Racks
L1 | 8 | 2 | 1 | 1 | 22
R1 | 8 | 2 | 1 | 1 | 22
L5 | 8 | 2 | 1 | 1 | 22
R5 | 8 | 2 | 1 | 1 | 22
1 rack = 600 x 900
Interlock Systems

## Slide 73
Location | Quench Detection Systems (QDS) | PIC | WIC/ FMCM | BIS | CLIQ
 | # of Racks | # of Racks | # of Racks | # of Racks | # of Racks
L1 | 8 | 2 | 1 | 1 | 22
Interlock Systems