## Slide 2: Tier-0 Resources
Helge Meinhard, CERN-IT
WLCG Management Board
14-Jul-2015

## Slide 3: Outline
Hardware status
VM performance
ATLAS tier-0 issues

## Slide 4: Hardware Status
Disk pledges: fully installed and available beginning 2015
Tape pledges: idem
CPU pledges
  27’000 cores delivered rather late
  After burnin, discovered that firmware upgrade was required – done during May
  Availability uncomfortably close to start of LHC data taking
  Now fully commissioned and in operation
  Hardware pledges fully met

## Slide 5: VM Performance (1)
Most CPU pledges provided as virtual machines
Compute cells: CPU pass-through, KVM caching set to write-back
  KVM caching gains two orders of magnitude in IOPS
  Precludes live migration
Overhead from virtualisation larger than expected
  See following results presented at a CERN-IT-internal meeting on 13-Jul-2015

## Slide 6: VM Performance (2)
Arbitrary hardware type with 32 cores, no further tuning (“type 1”)

## Slide 7: VM Performance (3)
Numerous handles to turn
Chart: HS06 - Percentage Overhead and HS06 ratings for full node VM (32x core Intel)
| Bare Metal CC7 | Bare Metal SLC6 | Default KVM | KSM off | +EPT off | + Pinning | +PAE
HS06 | 366.58 | 358.4 | 282.9 | 297.42 | 316.39 | 321.95 | 325.5

## Slide 8: VM Performance (4)
Tuning depends on exact hardware type
HWDB HS06 | VM Size (cores) | Per VM HS06 | Total HS06 | Overhead | Overhead Reduction
344±1 | 4x 8 | 84±7 | 336 | 2.3% | 65.7%
 | 2x 16 | 161±2 | 322 | 6.4% | 22%
 | 1x 32 | 279±4 | 279 | 19% | 13.6%
Type 1 optimised:
Type 2 optimised:
HWDB HS06 | VM Size (cores) | Per VM HS06 | Total HS06 | Overhead | Overhead Reduction
357±16 | 4x 8 | 87±11 | 348 | 2.5% | 68%
 | 2x 16 | 163.5±1 | 327 | 8.4% | 52%
 | 1x 32 | 311±1 | 311 | 12.9% | 37%
Intel(R) Xeon(R) CPU E5-2650 v2 @ 2.60GHz
Intel(R) Xeon(R) CPU E5-2630 v3 @ 2.40GHz

## Slide 9: VM Performance (5)
Optimised settings being rolled out across compute cells
Given core distribution of VMs, overall performance hit is ~7…8%
Reason for larger performance hit on large VMs (counter-intuitive!), and for hardware dependence, not understood yet
Why use large VMs at all?
  More flexible in context of multi-core (in particular 8-core) jobs
  LSF limit of 5’000 worker nodes per instance

## Slide 10: VM Performance (6)
Even though hardware fully deployed to meet pledges, shown effect means some ~10% shortfall in usable capacity
Some spare capacity being configured now, likely to get close to covering the shortfall
More CPUs (some 10’000 cores) coming up for delivery in September, likely to become available in October
Working on understanding the large performance hit, and on developing alternative scenarios in view of 2016

## Slide 11: ATLAS Tier-0 issues (1)
Separate LSF instance
  Protection against unforeseen user behaviour on shared instance
Started with 24-core workers with 480 GB of SSD disks
  Very little swap space: jobs killed frequently
    Tier-0 jobs need more than 2 GB in initialisation and termination phase
    Memory leak in application, fixed meanwhile
  Configured swap at expense of /pool: jobs killed frequently
    Not enough space in /pool
  Significantly improved pool cleaner, disabled core files

## Slide 12: ATLAS Tier-0 issues (2)
Instance beefed up by new 32-core machines deployed as 2 x 16-core VMs
  Performance ranging from 60 to 155 HS06
  Long (and painful!) investigations showed that CPU pinning introduced with OpenStack Juno was buggy – with 50% chance both VMs would be pinned to one and the same CPU, leaving the other idle. CPU pinning now deactivated
VM swapping causing up to 30% I/O wait
  See before for reasons and remedy
  Multi-core jobs much better
Hypervisor swapping, causing I/O wait
  Lack of memory on HV with KSM off due to memory remnants of KSM switched on before, fixed by re-activating KSM

## Slide 13: ATLAS Tier-0 issues (3)
Followed up by very regular (sometimes daily) meetings and phone conferences
Very good collaboration between ATLAS and the CERN-IT teams – big thanks to ATLAS
Situation now stable and workable

## Slide 14: Summary
Hardware fully put in place – disk and tape in good time, CPU rather late
Discovered unexpected significant performance hit on large VMs
  Tuning gets it down
  Capacity to compensate is on its way
  Efforts continuing
Long and painful (for ATLAS and CERN-IT) way to fully commission ATLAS tier-0 resources
Situation now stable and workable

## Slide 15: Questions?