## Slide 2: SM18 cryogenics infrastructure upgrade
L. Serio
TE-CRG

## Slide 3: Outline
Project definition
  Scope of work, limit of supply and interfaces
  Requirements and assumptions
  Estimation of the cryogenic loads based on
    Users planning and theoretical loads
    Benchmarking with measured data
Baseline conceptual proposal
  Phased implementation
  Budget and resources
Alternative scenarios parametric study
Risks and opportunities

## Slide 4: Scope of Work
Consolidation and upgrade of the SM18 cryogenic infrastructure
  for the HL-LHC Project and other large cryogenic capacity needs
  to cover the 2015-2023 period (and beyond ?)
The new infrastructure shall:
· increase testing rate and parallel testing capabilities -> increase LHe production and 1.8 K pumping capacity
· increase availability
-> implement redundancy
· fulfil cooling needs for IT String (3) (triplet Q, SC link and feed box)
-> additional and dedicated equipment

## Slide 5: Limit of supply and interfaces
Limits of supply |  |  | 
Magnet test stations |  |  | 
 | Vertical |  | 
 | Horizontal |  | 
 | SC links / IT String (3) |  | 
Cavity test stations |  |  | 
 | Vertical |  | 
 | Horizontal |  | 
Cryogenic test station |  |  | 
 | GReC |  | 
Cryogenics production |  |  | 
 | Helium liquefiers / refrigerators |  | 
 | compressor stations |  | 
 | purification system and balloons |  | 
 | L/G He and LN2 common storage |  | 
 | Warm and cold pumping units |  | 
 | Common valve boxes and TL |  | 
 | CWUs |  | 
Utilities |  |  | 
 | Cooling water |  | 
 | Electrical power distribution |  | 
 | Industrial controls |  | 
Interfaces |  |  | 
Magnet test stations proximity cryogenics |  |  | 
 | Vertical |  | 
 | Horizontal |  | 
 | SC links / IT String (3) |  | 
Cavity test stations proximity cryogenics |  |  | 
 | Vertical |  | 
 | Horizontal |  | 
Cryogenic test station |  |  | 
 | GReC |  | 
Utilities |  |  | 
 | Civil engineering |  | 
 | Cooling and ventilation |  | 
 | Electrical power distribution |  | 
 | Transport and handling |  | 
 | Integration |  | 
 | Platform and structures |  | 
 | Industrial controls |  | 

## Slide 6: Requirements and assumptions
  Baseline testing capability/requirement based on foreseen test plan (incl. other limitations) and theoretical loads (Q1-2014)
    Magnets: 2 Vertical and 2 Horizontal magnet cold / month (2 powering)
    Cavities: 1 cavity test/2 weeks; 1 module test every 6 months
    SC link or IT String (3)
      Integrated systems testing, commissioning and operation
      ‘demanding’ individual systems tests on dedicated facilities
    Apply 50 % contingency for
      Known unknowns
      (e.g. unplanned tests, repeated tests and low performing components)
      Unknown unknowns

## Slide 7: Estimated loads and capacity
Mini: lower consumption tests
Maxi: no HW limitation – all tests
AVG: assumptions and 1 month avg
Recommended installed: AVG + 50 % margin
LHe 4.2 K
VLP 1.8 K
new
existing
new
existing

## Slide 8: Cryogenics loads based on users planning [estimated theoretical loads and benchmarking]
6 kW Linde
6 kW Linde + new 35 g/s liquefier
Delayed start
Longer and delayed SD
New benchmark
point
WPU1 & WPU2
WPU1 + WPU2
WPU1 + WPU2 + WPU3
WPU1 + WPU2
WPU1 + WPU2 + WPU3
6 kW Linde + new 10 g/s liquefier

## Slide 9: Baseline conceptual proposal

## Slide 10: Proposed implementation plan
Phased approach with available resources (minimisation of risk and investment) :
  Review tests requirements, milestones and implementation plan
  Review availability (redundancy) requirements
  Implement instrumentation (HW and virtual) to control/optimise distribution
  Upgrade controls (advanced) to improve performance and optimize
  Upgrade VLP (interconnections) to increase capacity and availability
  New WPU and CWU
  New refrigerator
done
done
implementing
under study
under study
on-hold
on-hold
< 12 g/s @ 1.8 K
< 36 g/s @ 2.0 K
< 200 kW CWU
< 18 g/s @ 1.8 K
< 54 g/s @ 2.0 K
< 27 g/s LHe
< 300 kW CWU
< 18 g/s @ 1.8 K
< 54 g/s @ 2.0 K
< 60 g/s LHe
< 300 kW CWU
production capacity:
< 6 g/s @ 1.8 K
< 18 g/s @ 2.0 K
< 27 g/s LHe
< 200 kW CWU

## Slide 11: Budget and resources
Estimates for cryogenic production infrastructure
  Utilities and civil engineering tbd after reviewing global SM18 UPG project
  Doesn’t take into account String 3 resources needs and overlap
Budget and resources available for TE/CRG
  Conditional to smooth operation and maintenance of the LHC
  Conditional to successful implementation in 2016 of new CRG O&M contract

## Slide 12: Alternative scenarios parametric study
Scenarios:
Controls/instr.
Coupling WPUs
WPU3
New liq 10 g/s
New liq 25 g/s
New liq 35 g/s
New ref 6 kW
BASELINE
possible
recommended

## Slide 13: Risks and opportunities
RISKS
  Not finalised or changing requirements -> cost against performances (?)
    Existing test stands: configuration, test rate, planning and required parallelism
    Contingency for known unknown and unknown unknown
    What beyond 2024 ?
  Resources availability constraints
    Smooth operation and maintenance of the LHC / New M&O contract ?
    Other projects (e.g. HL-LHC, SM18 proximity cryogenics, String 3, HIE-ISOLDE)
    LS2 overlap and conflict
  Budget
    Review of global SM18 UPG requirements and impact on utilities and CE
OPPORTUNITIES
  String 3 delayed to 2021 / 2022
    Proceed with scenario 2 only
    Delay to 2016 the decision based on a comprehensive review of all costs of SM18 project
  Synergies with other projects
    HL LHC, FAIR (?)

## Slide 14: References
SM18 upgrade Project Plan
  https://edms.cern.ch/document/1488041/2
Presentation TE-TM
  https://edms.cern.ch/file/1373723/2/TE_TM_L_Serio_20140410.pdf

## Slide 16: boundaries

## Slide 17
WPU 1
WPU 2
By-pass valves
25 000 l LHe
dewar
Heater
New Compressors
New
cold box
HP
LP
LHe
heater 1
heater 2
WPU 3
heater 3
Compressors
6 kW Linde
cold box
HP
LP
LHe
Dryer
Pre/ads
SM18 Infrastructure
Purification
GHe Storage
GHe Storage
GHe Storage
LHe
GHe
LN2 Storage
Precooler
By-pass valves

## Slide 18
Horizontal magnets
Vertical
magnets
RF
4x h & 2 x v
SC link
String 3
SC helium
Shield
GReC
CWU 1
CWU 2
CWU 3
Proximity Cryogenics
Feed Box

## Slide 19: WBS
1 | PROJECT MANAGEMENT |  |  | 
2 | CRYOGENIC PRODUCTION AND DISTRIBUTION |  |  | 
2.1 |  | 6 kW LINDE LIQUEFIER |  | 
2.2 |  | 6 kW LINDE COMPRESSOR STATION |  | 
2.3 |  | new REF or LIQU. |  | 6 kW
2.4 |  | new COMPRESSOR STATION |  | 
2.5 |  | CWU 1 |  | 
2.6 |  | CWU 2 |  | 
2.7 |  | new CWU 3 |  | 100 kW
2.8 |  | main distribution valve box |  | 
2.9 |  | main distribution transfer lines |  | 
3 | PURIFICATION SYSTEM |  |  | 
3.1 |  | Purification system 1 |  | 
3.2 |  | Purification system 2 |  | 
3.3 |  | Recovery compressor 1 |  | 
3.4 |  | Recovery compressor 2 |  | 
3.5 |  | Balloon system |  | 
3.6 |  | impure storage |  | 
4 | STORAGE |  |  | 
4.1 |  | LHe dewar - 25'000 l |  | 
4.2 |  | LHe mobile dewar - 10'000 l |  | 
4.3 |  | GHe tanks |  | 
4.4 |  | LN2 dewars |  | 
4.5 |  | new GHe tanks |  | 
5 | 1.9 K pumping system |  |  | 
5.1 |  | Warm pumping unit 1 & heater |  | 
5.2 |  | Warm pumping Unit 2 & heater |  | 
5.3 |  | Refurbished (new) Cold Pumping Unit 1 |  | 
5.4 |  | New Cold Pumping Unit 2 |  | 
5.5 |  | New WPU cold distribution box |  | 
5.6 |  | New Warm Pumping Unit 3 |  | 6 g/s
5.7 |  | New Cold Pumping Unit 3 |  | 
6 | CONTROLS AND ELECTRICAL |  |  | 
6.1 |  | Controls upgrade |  | 
6.2 |  | New refrigerator |  | 
6.3 |  | New pumping Unit |  | 
6.4 |  | Infrastructure |  | 
7 | UTILITIES |  |  | 
7.1 |  | Civil engineering 250 m2 |  | 
7.2 |  | Controls and network upgrade |  | 
7.3 |  | Cooling and ventilation 2 MW; 100 kW |  | 
7.4 |  | Electrical power and distribution 2 MW |  | 
7.5 |  | Transport and Handling 20 t crane |  | 

## Slide 20: Review of client baseline testing program and consumptions
Estimates of the 4.5 and 1.8 K loads based on 2014 last quarter test plan
Comparison with measured loads
Extrapolation to 2015 – 2026 baseline test program

## Slide 21: Benchmark on 2014 tests: 4.5 K

## Slide 22: Benchmark on 2014 tests: 1.8 K

## Slide 23
Conceptual study ongoing for positioning of cryogenics infrastructure to supply IT String.
Very likely that a new building will be required.
SM18
SH18
cryogenics
SW18
Cooling water
&
Cryogenics
New refrigerator or liquefier
New WPU3
New compressor station
New compressor station
?

## Slide 24: Phase 3a
Cold by-pass for full redundancy between the heaters and WPU’s (check for use of existing interface box valves

## Slide 25: Phase 3b (ready for String 3)

## Slide 26: Upgrades and loads