## Slide 1: Safety considerations for SM-18 control room
Thomas Otto, HL-LHC PSO

## Slide 2: Safety role of control room
Operation:
  Provide safe and ergonomic working environment for operators controlling hazardous operations (cryogenic fluids, pressure, electrical current)
Emergency (fire, He-spill, …) :
  protect operators from adverse effects (projectiles, gas, smoke,…)
  Enable to safely control unaffected equipment and bring it into a safe state before evacuating
Ideal control room located in separate building

## Slide 3: Siting
Potentially
Large
Medium
Helium-spill
Present
Proposed
Control room
Evacuation
on ground
in 1st floor

## Slide 4: Interior of control room
Background noise ≤ 60 dB(A)
Ergonomic design of workstations
In principle, view on exterior for permanent workplaces for occupancy ≥ 2.5 days/week
Absence justifiable for control room (closeness to technical installation)

## Slide 5: Offices on Gallery ?
Not in line with safe and ergonomic design:
No view on exterior (and not justifiable)
Office workers exposed to SM-18 hazards