## Slide 1: Inner Triplet System
Recap Updates AMS/PM comparison
Unexplained anomalies
Further work
By Scott Rowan
TE-MPE-PE

## Slide 2: Recap
Last presentation found similarities in curve characteristics, including RQX bump, but rather inaccurate.
1st AMS/PM comparison, as of last month. (max error ~1kA)
AMS simulation result
(resolution of excel data)
RQX.L5 & RQX.R5 PM plot
RQX.L5/R5 PNO.D16, FPA at 90% Inom

## Slide 3: Reasons for Errors & Solutions thus far
Missing information on databases (design info as well as measured)
Miscalculation of resistances
Inaccurate parameters for thyristors/diodes
Low frequency simulations
Missing information resolved (to an extent) after further meetings with H. Thiesen
Recalculation with more accurate equations/resistance per unit length
Device modelling errors resolved by using excel along with the equation to establish the most pertinent. Trial and error optimisation in the AMS model editor was also used.
Use of ABM with break function to accurately measure specific points in a simulation without taking up too much time/memory…
e.g BREAK((TIME+300U)*FLOOR(TIME/679)*(1-FLOOR(TIME/700)))

## Slide 4: Updates - Schematic
Internal impedances
Cable/LEM resistances
Thyristor triggering altered
Cable/LEM resistances
Use of variable parameters

## Slide 5: Updates - Cable Resistances
RQX/RTQX2 busbar resistance taken from layout database
Use of various resistance per unit length gave results as follows:
Copper resistivity |  |  |  |  |  | 
 |  |  | Resistivity(Ωm) @20°C | 1.75E-08 | 1.72E-08 | 1.68E-08
 | Area (m2) | Length(m) |  |  |  | 
PURPLE | 2.40E-04 | 9 | Resistance(Ω) | 6.56E-04 | 6.45E-04 | 6.30E-04
ORANGE | 2.50E-05 | 9 | R=((pL)/A) | 6.30E-03 | 6.19E-03 | 6.05E-03
RED | 3.00E-04 | 1.5 |  | 8.75E-05 | 8.60E-05 | 8.40E-05
GREEN | 3.50E-05 | 1.5 |  | 7.50E-04 | 7.37E-04 | 7.20E-04
BAR | 2.50E-04 | 2 |  | 1.40E-04 | 1.38E-04 | 1.34E-04
Purple
Purple
Red
Orange: used for LEM par to FWD input
Green: used for LEM par to FWT input
Bar: used between RTQX1 and FWT

## Slide 6: AMS/PM Comparison
All tests carried out using given data for RQX.R5
Naturally these are tested against the PM data for RQX.R5 tests.
All test are programmed to be simulated but I will only present those I deem most important
PNO.D12/13
PLI3.D11
PNO.D16/17

## Slide 7: AMS/PM Comparison - PLI3.D10
Point of FPA
RQX & RTQX2 ramped to 50% nom
RTQX1 not in operation in this test
Max error 20A
(<1% of Imax)
Discharge time constants vary with time,
this explains the error and is most likely
minor changes resistance with thermal effects
or minor reduction in magnet inductance with
current increase
Ignore: script copy error

## Slide 8: AMS/PM Comparison - PNO.D12
Max error 20A
(<1% of Imax)
All converters ramped
to 10% nom before FPA
Point of FPA, note current stored in Q1
from RTQX1 transfer to RQX loop: less
resistance than thyr path

## Slide 9: AMS/PM Comparison - PNO.D13
All converters ramped
to 10% nom before FPA
Point of FPA, note current stored in Q1
forced to transfer to RTQX2 loop, causing drop in RQX
Max error 20A
(<1% of Imax)

## Slide 10: AMS/PM Comparison - PNO.D12/13 error
Note: minor errors with RTQX1 off are greatly
amplified when in operation, assuming main error
lies in FWD/FWT path

## Slide 11: AMS/PM Comparison - PNO.D16
All converters ramped
to 90% nom before FPA
Point of FPA, note current stored in Q1
chooses RQX loop rather than thyristor loop causing bump in RQX
Max error 80A
(<2% of Imax)

## Slide 12: AMS/PM Comparison - PNO.D16 error
Main error: due to time at which current
stops flowing through thyrsitor path. Main
Controlling parameter unknown (ideality
factor?)
Main time constant remains steady, small
discrepancies can again be explained to
thermal increase in resistance / current
decrease in inductance over time.

## Slide 13: AMS/PM Comparison - PNO.D17
Expected change in time
constant (large current test)
No idea, discovered yesterday

## Slide 14: Unexplained Anomalies
Discharge anomaly: shown with RQX.L5 to conform
Noticeable kink in simulation, somewhat corresponds

## Slide 15: Unexplained Anomalies
Apart from PNO.D17 RQX transient of course...
I_A measurements don’t correspond to I_MEAS, note in both cases I_MEAS reads above/below 0A
I_A RTQX1 in positive operation
always wavers from -2A-2A back
up to 10A before falling to 0A.
I_A RTQX1 in negative
operation oscillates for
10ms at 10-20A

## Slide 16: Unexplained Anomalies
RQX.R5 PNO.D13 09
RQX.R5 PNO.D13 11
RQX.R5 PNO.D12 09
RQX.R5 PNO.D12 11

## Slide 17: Further Work
Test circuit model against PM with ALICE/LHCb circuit set-up/parameters
Enquire about, study, and test inductance variance with current and resistance variance with temperature properly.
Begin quench modelling
Enjoy my holiday, going to Inverness then to a music festival in English...
Note: Full database of RQX circuit events is now available to me.

## Slide 18: ANY QUESTIONS?
By Scott Rowan
TE-MPE-PE
Thank you for listening
Thanks to... Emmanuele Ravaioli
Hugues Thiesen
Davide Valentinis