## Slide 1: 13 kA Energy Extraction LHC machine
Gert Jan Coelingh – Knud Dahlerup-Petersen – TE/MPE/EE

## Slide 2
Components of an EE system: switches, drivers (powering and control electronics), current distribution system, extraction resistors, supervision electronics, cooling facility, Interlock system, Data Acquisition electronics and auxiliary systems (e.g. over-current detectors, snubber capacitor banks, electrical protection.
Basic Requirements: Reliability of the release systems, continuous availability, low losses and radiation tolerance.
Some Key Figures:
  The 32 high current and 202 low current EE facilities in the LHC represent 310 tons of equipment.
  All main components are tailor-made to the application, off-the-shelf equipment did not meet the CERN specification.
  The total reference cost of the systems was 19 MCHF.
Store Energy:
      RB: 1’236 MJ at ultimate current -RQF/RQD: 24 MJ at ultimate current.
      600 A corrector circuits: up to 150 kJ
Locations:
  Even points: all eight UA galleries (RB, QF/QD, correctors)
  Odd points: all six RR tunnel extensions (RB, correctors), tunnel (RB power systems in R34, R37), UJ33 (RB controls, correctors).

## Slide 3
General lay-out with one series-inserted EE system. Ex: RQF/RQD
RB circuit with two series-Inserted EE
systems
EPC – Y. Thurel
Only series extraction used in LHC

## Slide 4: Dipole Switch array ~ 12 m2 ~ 24m3

## Slide 7: Control Power Electronics: 2 x 0.5m2; < 1m3

## Slide 8: Interface Electronics & Daq&M – 19 inch 6U crate

## Slide 9: RB Resistor Controls Module
Temperature monitoring,
Ventilation controls and monitoring,

## Slide 10: DQRB 1 - DQRB 2 - DQRB 3 oo 6

## Slide 11: Secondary water cooling system (low pressure)

## Slide 12
Extraction switch assemblies for the main circuits
Extraction resistors for the main circuits
Distribution bus
Breaker controls modules and sound shield
VAB49
Quad DQR’s
Dipole DQR’s

## Slide 13
Three Dipole DQR’s under test at IHEP, Protvino, RU
Double-storey enclosure containing DQSQF / DQSQD
Two 600A EE systems in one rack
Extraction switch in point3 ‘long’ version of busway
Two 600A EE systems under test at BINP, Novosibirsk, RU

## Slide 14: Quadrupole Resistor: < 1 m2 < 2m3

## Slide 15: Maintenance
Preventive maintenance (9 man-weeks/yr)
  Yearly overhaul and service on breaker contacts and springs.
  Yearly tests on individual systems
    (strong need of specialists (dying species) and expensive)
Corrective maintenance (<1/yr)
  If needed - strong need of specialists (dying species) and extremely expensive (beam dump or start-up delay)**

## Slide 16
List of principal Non-Conformities observed during hardware Commissioning and Operation of the LHC 13 kA Energy Extraction Facilities:
Unit / component | Non-Conformity | Origin / Reason | Cure | Follow-up / Consequences
DQRQ quad dump resistor unit | Wrong resistance value (3.4 mΩ instead of 6.6 mΩ) | Transport damage. Choc, breaking insulating parts inside the body | Repair made at CERN after replacement | Problem eliminated Now spare unit Fully conform
DQRQ dump resistor unit | Low insulation resistance to ground | Rusty water dripping from ceiling of UA27. | Cleaned after replacement | Problem eliminated Now spare unit Fully conform
DQRCS cooling station ‘Roese’. | Several alarms from compressor supervision | Regulation out of tolerance | All 16 systems are now supplied by LHC compressed air distr. Local compressor removed | Problem eliminated
DQRB – most LHC points | Wrong voltage measurement | Unknown at the moment | By elimination, still ongoing | Test to be performed during next TS
DQSB with closing problem | Holding coil had internal short circuit | Failure of wire insulation (enamel) | Breaker replaced | Unit awaiting new coil to be delivered
DQSB/DQSQ | Two issues with μ-switches | Lack of sealing by IHEP | Component replaced | Problem eliminated
BCM switch powering module | Spurious opening by slow release RR13 (S81) | Most probably bad contact in ‘holding’ circuit | Occurred twice, disappeared after dismounting / remounting | Stopped beam injection until re-closing

## Slide 17: All LHC systems’ circuit breakers
  ARE OBSELETE…
  Any new system means:
  R&D
  More for Semi-Conductor switches
  Less .. (but not negligible) for Electro-Mechanical Breakers
  Design of new systems on «Plug&Play» base for corrective maintenance
  3-5 years before version “0”

## Slide 18: Need to know
Does the magnet really need external energy extraction?
(parallel resistors as in corrector circuits)
If so
is crowbar resistor in power converter enough?
(max voltage over power converter during by-pass!)

## Slide 19: Need to know
EE design parameters depends on a variety of different requirements
Peak (ultimate) current & bi- or unipolar circuit
Maximum stored energy
Max time to open the switch (from conductive to isolation state) not including quench detection and verification (discrimination) time
Max admissible heat dissipation in a quenching element (and by-pass) before and during switching of the current to the absorber and during the decay (t to open and circuit time constant during EE)
the max admissible circuit voltage to ground at critical points in the circuit
sufficient margin to avoid (or to provoke) quench back
the max allowed cooling time of the absorber body (not only in the shadow of cryo-recovery!!)
impact on the correct function and performance of various other elements in the circuit
Sufficient power converter boost margin to cover semi-conductor switches (if chosen)