## Slide 1: YETS 2015-16: recall CMS plans
Top priorities:
-complete the cleaning /replacement of the cryo system (TE+EN+CMS )
-replace damaged cryo valve on 6000l dewar (Intermediate Cryostat) TE +CMS
-diagnose & fix water leaks & repair any collateral damage
Other activities (original YETS programme):
-left-overs/snagging from LS1 activities + prep for YETS 2016-17
-repair of RPC chambers damaged by ventilation incident on 4 Jan
-major cooling system maintenance including control system upgrade
-precautionary replacement of cooling block in ECAL power supplies
Before going any further….an important message of THANKS:
- for the excellent collaboration with TE & EN depts, as well as PH of course,
in attacking the serious magnet cryogenic problems in 2015.
- and for the cooperation we also had from BE dept (also the other LHC experiments)
in getting the best out of a rather sick CMS last year.
…thanks to TE colleagues for various material herein

## Slide 2: Cryo: Oil removal system
Oil removal equipment pressure and leak tested at factory.
Separator & Coalescer systems will both arrive end Jan.
New adsorbers
delivered to CERN
by Air Liquide

## Slide 3: Cryo: CV273 valve replacement: UXC
Replacement valve arrived at CERN.
All preparations for access to 6000l
Dewar complete by 18 Jan.
Repair started 22 Jan (when mech.
interventions on the cold-box
finished)
Tank casing lowered, MLI removed
Next task is to cut Cu heat shield

## Slide 4: Cold box open both ends
Warm end modifications
Cold end
modifications
Modifications to isolate cold client & divide into 4 circuits for cleaning

## Slide 5: CMS Endoscope check inside heatex’s
Clean except for
v. small metal chips
One small piece of
soft material
(few mm)
- likely MLI

## Slide 6: N2 pre-cooler leak repaired
Repaired by specialist company
-preliminary leak check looks good
-final check after CB cleaning complete
Exchanger accessed
Leak identified
Spot the welder : puzzle # 3

## Slide 7: Dryer condenser: installed USC -2

## Slide 8: Cleaning machine & fluid: USC -3
Installed & commissioned, circulation in 1st circuit started
Vertrel XF
solvent
drums

## Slide 9: Moment of truth: is there Breox in the solvent?
Bingo! strong Breox
signature….
Looks like we are on
the right track
Taking samples from full circuit
Preparing IR analysis
Awaiting result…..
This morning: 10am

## Slide 10
Planning for cold-box cleaning, J Bremer
18/11/2015
Planning for all CB intervention driven by the
“cleaning / drying” procedure
Consistent with planning within errors. Drying procedure is biggest uncertainty
28 March

## Slide 11: Water leaks seen near end of HI run
RE4 +
YB0 and YB-2 leak detection cables
2x lowest ME1/1 +
Puddles on X1 floor
Refill rate of yoke-endcap cooling circuit buffer tank

## Slide 12: Search for the leak on YE+1
…obvious where the water came out
YE1 disk (1500t) withdrawn from barrel
(beampipe in place)
--source eventually traced to chamber 13
Removed on Sat 23 Jan

## Slide 13: Corrosion, sediment at exit from YE+1
Plate sent to Chem
group for analysis
Deposit has high
Pb & B content

## Slide 14: Exit from YE+1 to vac tank

## Slide 15: Chamber 13
Removed Sat am – thanks to transport, CMS & HSE crews
Leak from internal joint
Is this a on-off (eg mech damage) or 1st
symptom of a generic corrosion problem?

## Slide 16
SL 10m
SL 10m
PX56 Plug OPEN
TX54 Plug CLOSED
RPC gas leak measurement
Wednesday
27. January 2016
Replace Barrel turbines
Houari
3. Move YE-1
Pascal + 2 Fsu 3h
4’. Install BP Column support
3VSC + Sandro + 1Altead 1h
5. Re-install HF+ I beams (near/far)
Eric + 3 Altead 2h
2. Move YE-2
Pascal + 2 Fsu 2h
4. RP Sweep VAC tank
RP 3h
1. Move YE-3
Pascal + 2 Fsu 2h
Activity on top of detector
Crane activity to be co-ordinated with CMS SAFETY
Next :open other endcap to attack collateral damage from water exit thru vac tank
Then : separate +z endcap disks (3 & 4) to check small RPC leak – correlated with main one?

## Slide 17: Can CMS stick to the nominal YETS schedule?
Chamonix mtg
21 Mar
18Apr
25 Apr
Latest date to start closing to be ready 21 Mar
Cryo system/cleaning/replacement: looking good….
finish valve repair in UXC: : mid Feb
finish cold box cleaning + new oil removal: end Mar
Water leak repair:
replace ME1/1 chamber 13 : end Jan
collateral damage clean-up : mid Feb
secondary leak (RE4) diagnosis & repair : mid Feb
Water leak precautionary measures (if generic fault)
no estimate yet –stay tuned please!!