## Version Change List
version | changed by | changes made
v0 | Dolph | initial version
v1.0 | Dolph | add items 4b and 4c; add further recommendation to item 4 on DUNE TPC vertical position; identify if change to existing and/or new requirements needed;
v2.0 | Dolph | add item 15 ventilation barrier wall
v3.0 | Dolph | closed item 9; added "action/assign" throughout
V.3.1- | MVD | added comments after the first meeting of the Civil/Cryo working group
V.3.2 | MVD | added control room sheet for comments.

## ISSUES LIST
item # | title | description | ref docs | action assign | jjd notes | status and notes | DOCDB reference and action | Persons responsible
1 | DUNE grounding and shielding throughout campus | detector grounding and sheilding very incomplete from TPC (APA, CPA, field cage, ground plane), to HV, to cryostat, to cavern, to cryogenics systems, to electronic racks all the way through UG control room to transformers | change to requirements and interface ref doc-7310 (needs migration, relink and control) | DUNE initiate Change Request | impacts FSCF requirements, absolutely urgent with many very diverse opinions; professional evaluation and recommendation: cryostat pump grounding must be carefully considered | Tshaw: Grounding and shielding committee exists. Significant work done since this list was generated. | DOCDB-285 | Terry Shaw
2 | electronic racks power and cooling | DUNE desires increase in rack supply power; impacts power and ventilation requirements; may eliminate rack's local cooling, request lower cavern temperatures; | change to existing requirements and ICDs | DUNE initiate Change Request | impacts FSCF requirements, absolutely urgent with many very diverse opinions; my engr contribution is: ARUP cavern HVAC and vent reanalysis req, elect supply reeval req | We are waiting for input from Giles Barr to complete this. There will be better handle on this number. We may needs to be more general regardingthe function of each room. Jim has asked for providing envelope numbers for power in utility cavern, detector cavern, and surface facilities. A matrix would be useful in which for each space the requirement for power, ventilation, water, temperature, humidity, sound noise level, other characteristics, are identified. | exists | Terry Shaw
3 | UG control room requirements | everything from location accommodating LBNF&DUNE construction logistics to power to a/c to size to interface with cryo and CF needs resolution | change to existing and new requirements needed; change ICDs | DUNE initiate Change Request for all UG control room requirements additions and changes | location is OK wrt CS installation which comes well before room; location may not be OK wrt other issues; control room grounding must be considered | This is part of the DAQ design and discussion regarding location of various equipments. Giles and group must provide foot-print that could go from 0 to 1000 ft^2?. This also depends on whether CRYO control room will be in the same place. A process is needed to resolve what will be in control room: DAQ, CRYO. Function of the crontrol room is not know ! Decision is needed on what is needed in that control room ? Someone has to contact Barry and or David Montanari. MVD will contact CRYO people to make a decision. Does control room need to be a general gathering place ? Is this also place for meetings ? Quiet place to go think about things during installation => office space ? | MVD will make a sheet with all the intended functions for control room and distribute for comment and resolution. . DOCDB interface document 11202. ARUP plan is much larger room than 11202. | MVD will create a spreadsheet of requirements. All WG are required to provide information here.
4 | cryostat pumps and manifolds | requirement is very tight for FD thermal and phase stability, is this necessary? Requirement reads "The cryostat and cryogenic systems shall be designed to maintain a single phase in the entire liquid argon volume at a stable temperature." Rationale states "The chosen temperature is 88.3+-1 K" | change to existing requirements and ICDs | DUNE initiate Change Request | Professional evaluation and recommendation: temperature requirement is driver over purity for internal cryostat LAr flow (re: pumps and manifold); purity MUST be taken into account but will be qualitative to end of CF Final Design and must be approvable by DUNE earlier than that; CFD w/thermodynamics of cryostat is urgently needed, CF considers offering contact w/ME via ARUP to speed analysis; CFD recommended to focus on internal manifold changes with same number of (4) pumps in 3m space therefore no impact on CF; additional peripheral pumps and/or increase insulation thickness is an absolutely last resort; DUNE consideration to raise TPC closer to roof should be avoided to allow potential manifold changes | We need claification of what the concern from the CRYO group. A physics impact analysis needed to soften this requirement. And a firm counter proposal is needed about how much to soften the requirement. MVD will follow through on how this requirement traces back and make a list of scientific issues that must be studied. I How is the temperature control achieved ? When will be a CFD analysis done ? What does it mean that DUNE initiate change request ? | MVD and RUSS will call Barry and ask what is going on. A spreadsheet of concerns will be created | Russ Rucinsky, MVD, and BN with consultation with Bo Yu and Craig Thorn.
4b | detector installation and cryostat annulus space | add requirement for detector installation through a cryostat temporary construction opening; Alimak lift assumed acceptable and achievable in 3m space | change to existing and new requirements needed | DUNE initiate Change Request | Professional evaluation and recommendation: single 3m space will be very restrictive with this addition, consider putting this addition or two of the four pumps at the other end in additional 3m space | This is a requirement that comes from the dual phase initiative. Perhaps it should be worded more broadly since the installation plan for dual phase may evolve as the design evolves. | Need some document about dual phase installation. | Assigned to Jim Stewart and Jack Fowler.
4c | cryostat pumps and manifolds #2 | DUNE-LBNF requirement LArFD-L2-Cryo-14 for low flow speeds needs flow variability tolerance to limit drift distortion | LArFD-L2-Cryo-14; new: larfd-l2-se for drift distortion, FD-engr for LAr flow, elect field distortion and TPC mech stability | DUNE initiate Change Request | Professional evaluation and recommendation: manifold efficiency decreases with length, move two pumps to opposite end of cryostats; potential impact on CF of all three items is too great to ignore a need to at least increase the cavern lengths by 3m at West and East ends | Flow variability tolerance. What level of analysis is needed ? Drift velocity is 1.6 mm/microsec. MVD will contact Bo Yu and ask what this specification should be. May need to wait for the CFD analysis. This impacts CD3a in terms of 3 meters at end of detector away from the pillar. CDF decision will be in December. | Cannot close by the review. By back of envelop calculations can state that convection governs the local flow and not pumps. The requirement seems strangely written. May be it got garbled during many changes. | Bo Yu, Russ Rucinscki, Barry Norris
5 | detector/cryostat/cavern alignment tolerances | requirement is beam bearing +- 5.8 degrees implied to be whole campus but cavern to cavern relative tolerance TBD; | change to existing and new requirements needed | DUNE initiate Change Request to add cavern to cavern relative tolerance and if bearing angle tolerance changes | Professional evaluation and recommendation: this requirement needs to be defined by DUNE after review of all survey activities to be accomplished in near future; recommend requirement be based on the best that can be accomplished after near-term survey and excavation capabilities | The 5.8 degree tolerance is for each cavern. No other requirement is needed. Statement needed why any tolerance is needed between caverns. Scientific rationale that is motivated by the highest priority science is needed to place a requirement on relative cavern to cavern alignment. | Closed
6 | detector/cryostat/cavern level tolerance | cavern floor spec cryostat shim limits and cryostat roof deflections are all issues | change to existing and new requirements needed | DUNE initiate Change Request to identify roof level and waviness requirement that will flow down to cryostat and CF | Professional evaluation and recommendation: above concrete normal and standard tolerances increases cost; shim thickness limits likely to be small, structural analysis will need to be done, shimming to avoid point loads which add large local stress to concrete and cryostat, rock likely not affected if no concrete but need grout; roof level and waviness specification urgently required from DUNE; request for cryostat roof deflection decrease increases the beam moment of inertia is adverse impact to LBNF | These are detailed engineering issues for single phase. Are these more restrictive for dual phase ? Suggestion: the cryo engineering team should resolve these issues as part of cryostat preliminary design and CF final design. Write down a list of specifications needed and produce an initial proposal. CavernFloorXcryostat: Tracy and Dmitar CavernRoofXcryostatL: tracy + dmitar+ Jack | Another set of separate meetings to resolve these details. Include dual phase folks. | Tracy, Dmitar, Fowler, Russ
7 | cryostat bridges | confirm that the bridges, each ends, between the cryostat and rock/concrete floor is outside of CF scope and will not affect CF scope (such as adding a need for support connections) | change to existing and new requirements needed | DUNE initiate Change Request to add requirement for bridges | decision required, LBNF cryostat accept design and construction? grounding approval required from DUNE | Russ states this is taken care of in the interface control document. Terry states that as long as ground isolation is not affected DUNE approves this change. Jim Stewart: no guard rails along the top or on the pillar. Please add guard rail requirement. | ICD document dcdb-102. Russ shall add guard rail issue to the ICD. Grounding document 285 . Clsoed after followup regarding guard rails. | Terry Shaw for followup.
8 | clean room interference | confirm that the temporary clean room for detector assembly will not affect CF design | note in ICD | DUNE review ARUP 100% | study and decision required by DUNE | If there is a temporary clean room it will be placed over the pillar and cryostat hatches. Confirm this idea. Russ will add this to the ICD. And state that this will not affect CF. There is a line item in power spread sheet for the clean room. Blow air through cryostat and comes out the hatch into the clean room. For the dual phase TCO the scheme might be different. | ICD documents need to include this issue. And Russ requests that a short memo be produced regarding various options of the clean room for single and dual phase. | Marco and Sebastian from Dual phase need to respond. Russ will be point man from this group.
9 | utilities and cryo piping across caverns 1&2 ground isolation | define whether passing supply power, argon and nitrogen gas pipes, water pipes, etc across the first chamber is acceptable from a ground isolation perspective - or define requirements for isolation from the mesh if needed. | change to existing and new requirements needed | CLOSED | study and decision required by DUNE | closed - no special grounding required per Josh & Terri email 9/9/15. Terry had a solution and it is in the grouding document | dcdb-285
10 | mezzanine requirements | LBNF mezzanine proposal for east and west detector cavern ends | new requirements needed | LBNF initiate Change Request | study to define requirements and decision required | JimS: LBNF cryo needs to inform LBNF CF about the what is required on the mezzanine regarding cryo equipment. It is the gas purification system. Are there any interferrences with the electronics racks in the mezzanine ? We do not want any connections from the mezzanine to our detector grounding. Grounding issue is well defined. Mezzanine needs to be connected to cavern ground. Cavern ground is not same as detector ground. | dcdb-285. Drawing in BSI has details of clearance. Russ shall confirm | Russ will follow up regarding this in the ICD add some clearance for our racks and will communicate with Cryo team to make sure they followup.
11 | cryostat structure components down shaft and into caverns | large dimension steel beams and columns require headframe and shaft modifications, and engineering plan for monorail hoisting into detector caverns | new requirements needed; revise ICDs | LBNF initiate Change Request | Professional evaluation and recommendation: Yates shaft brow modification impacts are high; Ross shaft plan already in place and should be the limiting size requirement | No issue here for DUNE. This is a inteface between LBNF CF and LBNF cryo. |  | Not assigned.
12 | drift cross-section reduction | cost savings to excavation needs evaluation by cryo systems and DUNE | change to existing requirements; revise ICDs | LBNF initiate Change Request | study and decision required material logistics through drifts | There is an ICD between DUNE and shafts. Accomodating the largest item for DUNE which is the APA shipping container. DUNE is not ready to confirm this change now. A full model of installation and integration is needed including a design for the proper conveyances. | memo is needed to put this off. Configuration change control database will have an entry reagrding this change. Eric James | Eric James and Jim Stewart, Russ will put the information in the database.
13 | all monorail uses and locations | additional to item #11 decision required by LBNF and DUNE | change to existing requirements; revise ICDs | LBNF initiate Change Request | study and decision required material logistics over rock pillar | Russ: monorails are in the requirements. This is focusing on cryostat construction. Is there a spread sheet regarding all uses of the monorail ? There is a hoisting and crane coverage docdb. DUNE plans to use the monorails for moving racks. Make clear in the ICDs that transportation of detector equipment will include east and west drfits. And so some monorail use will be needed by DUNE. | dcdb-11215, Clarify in the ICD the use of monorails for detector equipment. | Assigned to Russ to find the proper ICD and find what change LBNF wants.
14 | ventilation around cryostat annulus and base | prevent condensation and freezing after all annulus and base space considerations above | potential change to requirements; potential revise ICDs | LBNF initiate Change Request | Professional evaluation and recommendation: CFD must adjust to all related changes above | Relevant to LBNF CRYO. Need to keep abreast |  | Zelimir/Montanari
15 | ventilation barrier wall | segregate air spaces above each cryostat | change to requirements and ICDs | DUNE initiate Change Request | study and decision required based on air quality in cryostat during and after membrane installation and cleaning | Relevant to LBNF/Cryo. Need to keep abreast. |  | Zelimir/Montanari
16
17
18
19
20
21
22
23
24
25
26

## Control Room Req.
ID | Type | Object Heading | Object Text | Rationale | Notes | Parents | Parents | Verification Method (VM) | VM Work Assignment | Person assigned
Crtlrm-Lx-1 | Definition | Underground control room definition | Underground control room shall serve as a central place from which various functions of the far detector facility shall be monitored and controlled. | We need to define all function of this space before construction since expansion of this space is difficult in the future. The control room space may be subdivided further to serve each individual need as specified below. | This space must be adequate for 4 single phase detectors since this is considered the worst case in terms of space.
crtlrm-lx-2 | requirement | control room cable trays and services | Control room shall have adequate space for all entering and existing cables, and services. | The cables include data cables from the detector cavern, control cables, power cables for cotrol room equipment, communication cables, safety related services, any special purpose services such as gas, water. | This list must be made and maintained. |  |  |  |  | Terry Shaw
crtlrm-lx-3 | requirement | control room DAQ electronics racks | Control Room shall have space for electronics racks for the DAQ system | Number of racks are to be specified according to the DAQ model adapted | [5 empty] | Terry with Giles
crtlrm-lx-4 | requirement | DAQ computer systems and local data storage, network services | The control room shall accommodate DAQ computer systems, data storage and netwok services | Computer systems, power requirement, and environmental requirements for long term operation are to be specified. | [5 empty] | Terry and Giles
crtlrm-lx-5 | requirement | Cryogenic control electronics racks | Control room shall accommodate electronics racks for cryogenic system controls. | [6 empty] | Barry Norris and Russ
crtlrm-lx-6 | requirement | cryogenics controls station | Control room shall have a control station with monitors and keyboards, etc for cryogenic equipment. | [6 empty] | Barry Norris and Russ
crtlrm-lx-7 | requirement | central location for information through bulletin boards, online systems, monitors | Control shall have adequate provisions for bulletin boards, monitoring displays, and other systems for information exchange. | [6 empty] | Russ and others will just specify
crtlrm-lx-8 | requirement | central location for informal gathering | The control room shall accommodate the need for informal small meetings of the staff during operations. | [6 empty] | Will specify collectively the number of people.
crtlrm-lx-9 | requirement | central lcoation for daily meetings during installation | The control room shall contain the provision for daily meetings of the staff during installation and commissioning | [6 empty] | Will specify the number of people.
crtlrm-lx-10 | requirement | DAQ control stations | The control room shall have adequte number of control stations with monitors, keyboards, etc. to control the DAQ. | [6 empty] | Giles and co-conveners.
crtlrm-lx-11 | requirement | Fire life safety equipment racks | Control Room shall contain racks to house the control equiment and monitoring devices for fire and life safety related to the cryogenics and Far Detector only. | [6 empty] | This is part of SURF. Do we need space for this in our control room. Ask Tracy + Josh.
crtlrm-lx-12 | requirement | Fire and life safety control station | Control room shall contain a control station with monitors and keyboards, etc for fire and life safety | [6 empty] | This is part of LBNF and SURF. Ask Tracy and Josh.
crtlrm-lx-13 | requirement | common work spaces for visitors | Control room shall contain adequate number of common work spaces with network, phone, and power with appropriate environment in terms of temperature, ventillation, and noise. | [6 empty] | Lets have space for 15 people. Specified by the FDCCI group.
crtlrm-lx-14 | requirement | Logbook storage | Control room shall have adequate shelf space for paper logbooks, manuals, stationary, etc | [6 empty] | 1 large bookcase needed.
crtlrm-lx-15 | requirement | Calibration and testing equipment space | Control room shall have adequate shelf space for storage of appropriate amount of calibration equipment and tools only for FD calibration tasks | [6 empty] | The space on top of detector will be used for this equipment. No space needed in the control room.