## Slide 1
TE/MPE/ee
FAIR Test Benches - update by 14 October 2015
K. Dahlerup-Petersen TE/MPE/ee – 14 October 2015
LHC Machine
Update and status for the Work Unit ‘Energy Extraction’
equipping the three test benches for series testing of Super-FRS Dipoles D2, D3, D4 and Quadrupoles Q3, Q4, Q5, Q6
in B180
The inventory of 600 A Extraction Switch Systems comprises today 22 complete units - intended as spares for LHC (16 systems) and reserved units for the three S-FRS test benches (6 systems)
Every system has been upgraded for conformity with the LHC/LS1 standards and corrected for some closing problems
The systems are presently subjected to an endurance test (‘on’ state for one month with acquisition activated)
Six units will then be selected for FAIR for further routine tests at rated current and precision measurement of the commutation process – prior to delivery and insertion into the test benches
The appointed test engineer (Szymon Michniuk/AGH) arrived to CERN on 1 September. Together with members of the MPE on-call team he shall perform the final program of routine testing
The 6 systems will be ready for installation in B180 on 1 Dec. 2015. To be completed by 30.04.16 as planned.

## Slide 2
TE/MPE/ee
FAIR Test Benches – update by 14 October 2015
K. Dahlerup-Petersen TE/MPE/ee – 14 October 2015
LHC Machine
DQR – extraction resistors:
3 x 2 units of 1.4 Ω, 2 MJ are foreseen. They are based on the use of carbon discs as the energy absorbing body. With natural air cooling by convection
2 prototypes arrived in August from Industry. After power testing (November 2015) the rest will be ordered (lead time: 6- 8 weeks)
The aluminium terminals will require bi-metallic cable lugs
Testing shall include verification at full energy deposit
The tested systems shall be ready for installation and connection in B180 by early January 2016