## Slide 1
Machine Protection and Interlocks
for Linac4

## Slide 2: Beam Interlock System : Backbone of the LHC Machine Protection
BIS
LBDS
Injection
Kicker
PIC
WIC
BLM
Collimation
FMCM
Other elements:
BLM : Beam Loss Monitors
Collimation system
FBCM: Fast Beam change Monitors
LBDS: LHC Beam Dumping System
FBCM
Machine Interlock Systems:
BIS : Beam Interlock System
FMCM : Fast Magnet Current change Monitors
PIC : Powering Interlocks Controllers
WIC: Warm magnet Interlocks Controllers

## Slide 3: BIS for LHC rings : the connected systems
Beam Interlock System
PIC essential
+ auxiliary
circuits
WIC
QPS
(several 1000)
Power
Converters
~1500
AUG
UPS
Power Converters
BLM
Vacuum
System
Vacuum
valves
Access
System
BPM in IR6
Access
Safety
Blocks
RF Stoppers
Magnets
Doors
EIS
Beam
Dumping System
FMCM
Cryo
OK
Injection BIS
Monitors
aperture limits
(some 100)
Monitors in arcs
(several 1000)
CCC
Operator Buttons
Transverse Feedback
Movable Devices
Beam
Aperture
Kickers
SMP
Experiments
BCM
Beam Loss
Experimental Magnets
RF
System
FBCM
Lifetime
Collimation
System
Collimator
Positions
Environmental
parameters
BTV
BTV screens
Software
Interlocks
LHC
Devices
Timing System
(PM)
Based on a R.Schmidt’s drawing
SEQ via
GMT
LHC
Devices
LHC
Devices
Timing
Safe
Beam
Flag
MKI
Mirrors

## Slide 4: BIS for Linac4 : the connected systems
Beam Interlock System
WIC
Power Converters
BLM
Vacuum
System
Magnets
Choppers System
CCC
Operator Buttons
Beam
Stoppers
Beam
Destinations
( via Timing system )
RF
System
Software
Interlocks
L4
Devices
L4
Devices
Linac4
Devices
External
Conditions
( via Timing system )
Pre-chopper System
L4
Source
BCT
(“Watch Dog”)
Linac4
Dump

## Slide 5: BIS : (# of LHC channels) Vs. (# of Linac4 channels)
17 Controllers for Beam-1
17 Controllers for Beam-2
+
4 Controllers for Linac4 only*
(*) Transfer line to Booster not included
~220 Interlocks connections from LHC systems
(beam-1, beam-2, both beams)
~30 Interlocks connections from Linac4 systems
Ring architecture
Tree architecture

## Slide 6
User Interfaces
User_Permits
#1
#14
#2
(installed in User’s rack)
Beam Interlock Controller
(VME chassis)
User System #1
User System #2
User System #14
front
rear
FESA class
copper cables
or
fiber optics links
Remote User Interfaces safely transmit Permit signals from connected systems to Controller
Controller acts as a concentrator,
  collecting User Systems Permits (14 HW + 1SW)
  generating local Beam Permit
Controllers linked either in Tree or in Ring architecture
JAVA
Application
Configuration DB
Software
Interlock
input
Technical
Network
Optical
outputs
(local )
Beam Permit
Cupper links
Beam Interlock System : simplified layout

## Slide 7
User Interface
Redundant
P.S.
Manager
Test & Monitoring
Back Panel
F.O. variant of
the User Interface
Optical daughter cards
Controller’s side
User system’s side
Beam Interlock System : the main Hardware boards

## Slide 8
Beam Interlock Crate
Front view
Rear view

## Slide 9
Quick overview of Beam Interlock System
The main features

## Slide 10
AND
User
Systems#n
User
Systems#3
User
Systems#2
User
Systems#1
“Actuator“
Σ (User Permit = “TRUE“ ) → Beam Permit = “TRUE“
( Injection Kicker
or Extraction Kicker
or Dump Kicker,
or H- source, etc…)
User Permit
inputs
Beam Permit
output
the BIS principle

## Slide 11
AND
User
Systems#n
User
Systems#3
User
Systems#2
User
Systems#1
“Actuator“
Σ (User Permit_A = “TRUE“ ) → Beam Permit_A = “TRUE“
( Injection Kicker
or Extraction Kicker
or Dump Kicker,
or H- source, etc…)
User Permit
Inputs_A & _B
Beam Permit
Output_A
Full redundancy
2
2
AND
Output_B
Σ (User Permit_B = “TRUE“ ) → Beam Permit_B = “TRUE“
Matrix_A
Matrix_B

## Slide 12
x 6
x 17
Input#1
Input#14
BIC
Screen shot of the Supervision application
Screen shot of the Supervision application
Scalability & Ring Architecture

## Slide 13
«Actuator system »
1
14
“Master” BIC
1
14
User Systems
1
14
Tree architecture is used in Linac4 and for the SPS to LHC Transfer lines
Scalability & Tree Architecture
“Slave” BIC
“Slave” BIC
  Slave BICs: AND operation of 14 +1 inputs
  Master BIC: AND and OR operations possible
    Inputs: either outputs from Slave BICs or additional USER_PERMIT inputs
SW
SW

## Slide 14
User System
to Controller
Front view
rear view
Could be PLC based, or VME based, or any type of electronics…
User
_
Permit
_
A+
User
_
Permit
_
A-
User_Permit = “FALSE” if Input current < ~10mA
User_Permit state transmitted in RS485 format
Standard HW solution for connecting any User System via a copper cable [ F.O. variant available for long link (>1.2km) ]
Unique Interface with the connected systems

## Slide 15
All LHC systems connected to the BIS in using the same Hardware interface
Beam Interlock System
PIC essential
+ auxiliary
circuits
WIC
QPS
(several 1000)
Power
Converters
~1500
AUG
UPS
Power Converters
BLM
Vacuum
System
Vacuum
valves
Access
System
BPM in IR6
Access
Safety
Blocks
RF Stoppers
Magnets
Doors
EIS
Beam
Dumping System
FMCM
Cryo
OK
Injection BIS
Monitors
aperture limits
(some 100)
Monitors in arcs
(several 1000)
CCC
Operator Buttons
Transverse Feedback
Movable Devices
Beam
Aperture
Kickers
Safe
Mach.
Param.
Experiments
BCM
Beam Loss
Experimental Magnets
RF
System
FBCM
Lifetime
Collimation
System
Collimator
Positions
Environmental
parameters
BTV
BTV screens
Mirrors
Software
Interlocks
LHC
Devices
Timing System
(Post Mortem)
LSA
LHC
Devices
LHC
Devices
Timing
Safe
Beam
Flag
CIBU
CIBU

## Slide 16: Very low contribution to overall LHC operation unavailability
Courtesy Chris RODERICK
Machine Protection system =
Beam Interlock System
+ Powering Interlocks
+ Warm magnets Interlocks

## Slide 17
Dependable: By design (SIL3 was used as a guideline) the system must react with
a probability of unsafe failure of less than 10-7 per hour;
Beam abort less than 1% of missions due to internal failure (2 to 4 failures per year)
Simple: On purpose, its just a “Go / No Go” system together with an ‟ AND‟ function and no more ! For a protection system: the Simplest is always the Best
System Performance (I)
“Flexible”:
since half of User Permit signals could be remotely masked by an Operator
(the other half, i.e. the critical ones, can be never masked)
Condition = “Safe Beam Flag” state;
If FALSE => masks are no longer taken into account
For LHC, “Safe Beam Flag” is derived from beam intensity and energy

## Slide 18
Safety process by Hardware:
Functionality into 2 redundant matrices with VHDL code written by different engineers following same specification
Critical versus Non-Critical:
At conception level, monitoring elements are separated from the 2 redundant safety channels
System Performance (II)
Fast: few μS from User Permit change to Local Beam Permit change

## Slide 19
100% Online Test Coverage:
easily tested from end-to end in a safe manner
=> recovered “good as new”
“Monitorable”:
any Input/output changes are logged into
an History Buffer with precise time stamping (UTC time with 1μS accuracy)
Reliable:
whole design studied using Military and Failure Modes Handbooks
Results from LHC analysis are:
P (false beam dump) per hour = 9.1 x 10-4
P (missed beam dump) per hour = 3.3 x 10-9
System Performance (III)

## Slide 20
Operational Tests
Configuration verification and integrity checks
Fault Diagnostics and monitoring
Response Analysis
Pre-Operational Checks
Checks during Operation
Post-Operational
Checks

## Slide 21
Kernel of LHC Post-Mortem Analysis
Identification of the Beam Dump source
Reconstruction of the sequence of events that has led to the beam dump
the different History Buffers are gathered and analysed by the Post-Mortem system

## Slide 22
BIS for Linac4 and Booster : the Interlock zones
The Linac4 interlock zones :
The PS Booster interlock zones :

## Slide 23
Main constraints:
  Multiple ‘interlock zones’ due to several destinations
    Destinations for Linac4: L4DUMP, LBE, PSB
    PSB destinations: BDUMP, ISOGPS, ISOHRS, PS
  PSB is the (timing) master of Linac4
    Maximise proton delivery via ‘External Conditions’;
    Beam stoppers and bending magnet rise-time too slow
PSB and Linac4 interlock systems have been considered together
BIS for Linac4 and Booster : the design principle (I)
Note: The Beam Interlock System is not involved in personnel safety !

## Slide 24
BIS for Linac4 and Booster : the design principle (II)
Three main components:
  Hardware interlock system (BIS): reliable, fast
    For fast reaction times
    If considered useful to avoid machine activation
  Software interlock system (SIS): flexible
    For slow-changing parameters
    If some more complex logic needs to be adopted
  External conditions (EC): for proton optimization
    Consider user requests
    Method also useful for Booster ring-specific interlocks
    The “user” (+beam destination) is calculated for the current cycle depending on some necessary conditions;

## Slide 25
BIS for Linac4 and Booster : the global layout

## Slide 26
… the Linac4 layout only : Tree Architecture

## Slide 27
Magnet Interlock System for Linac4

## Slide 28
Warm Magnet Interlock Controllers : quick overview (I)
Standardized interlock system for normal conducting magnets based on Programmable Logic Controllers (PLC):
  Collects inputs from thermo-switches, flow switches and internal PC faults
  Provides Permits to the power converter and beam interlock system
Configuration DB
Beam Permit
Generic Solution => deployed from Linac4 up to LHC

## Slide 29
Warm Magnet Interlock Controllers : quick overview (II)
Remote test feature
Thermoswitch –
ELMWOOD
Type 3106 – T117
Magnet Interlock Box
with (single) sensor
connectivity and remote
test relay
Magnet Interlock SCADA System
Beam Permit towards BIS

## Slide 30
That’s all !
Thanks for your attention

## Slide 31: Additional slides

## Slide 32: Linac4 BIS (1)
Master BIC ‘Source RF’
  Action: switch off the source RF voltage (~10 μs reaction time)
  Redundant action: pulse pre-chopper (use timing signals NX.STOP(START)-PCHOP); ~2 μs rise-time

## Slide 33: Linac4 BIS (2)
Master BIC ‘Choppers’
  Action: pulse pre-chopper (use timing signals NX.STOP(START)-PCHOP); ~2 μs rise-time
  Redundant action: pulse chopper; a few ns rise-time
  Disable start timing of PSB RF if possible

## Slide 34: Linac4 BIS (3)
Slave BIC ‘Linac4 and Linac4 Transfer OK’
  Input for Master BIC ‘Choppers’
    L4 Magnet Current Status: AQN of main bendings surveyed with FGCs depending on destination (OR of digital output signals if AQN outside window ~1 ms before beam pulse)
    EC only if all rings affected (e.g. user requests; see later)

## Slide 35: Linac4 Software Interlocks (SIS)
  Action depending on Master BIC affiliation
  List not exhaustive!

## Slide 36: PSB Injection Software Interlocks (SIS)
Output connected to Slave BIC ‘PSB OK’
  Action defined by Master BIC ‘Choppers’ (pre-chopper, chopper and PSB RF)
  List not exhaustive!
  WIC information to be transmitted to SIS

## Slide 37
Application view of the USER_PERMIT signals for the ‘Source RF’ Master BIC used for the commissioning phases

## Slide 38
Timing diagram of the USER_PERMIT signals FOR the ‘Source RF’ Master BIC

## Slide 39: BIS : standard solution from LHC down to Linac4
  Same Hardware:
    Fast, Safe, Reliable (initially designed for LHC)
    Standardised interface (CIBU)
    Proven solution
    Cost-effective
  Same Monitoring Software:
    Unique application in CCC
    100% Online test coverage
  Operational flexibility
    Software Interlock Inputs
    External Condition signals used as User_Permits
    Masking available on half of input channels

## Slide 40
The reaction time
Actuator

## Slide 41: BIS Application : Monitoring of the Inputs/Outputs state

## Slide 42: BIS Application: History Buffer

## Slide 43
Only 7 out of 14 inputs can be masked by the Operator
Masking automatically removed when “Safe Beam Flag” = FALSE
The “flexibility” : Masking of input(s)

## Slide 44: Safe Beam Flag
For LHC: the Safe Beam Flag (SBF) is produced by a dedicated system (Safe Machine Parameters Controller)
Based on Beam Energy and on Beam Intensity:
  if ( I · E < defined_Threshold ) then SBF = “TRUE” ; else SBF = “FALSE”
The SBF value is transmitted to the LHC Timing generator
=> information broadcasted over the GMT network.
Timing receiver installed in the BIC chassis gives the corresponding Hw signal value
Note: Safe Beam Flag for SPS only depends on beam intensity.