## Slide 1
SMART INTERFACE
A Modular Monitoring Station

## Slide 2
Background
2011: The need of a new Modular Monitoring Station was expressed
within the CERN HSE Unit
Smart!
Modular
Ok
Reliable
New
And
Need
Station

## Slide 3
Background
2013: The SMART Interface was designed at CERN to have the
full control of the system
Reliable
Modular
Online diagnostics
5 days data backup
Easy to install
Checking communication
SCADA
Ethernet
Network
Measuring
Equipment
SMART

## Slide 4
Objectives
SMART Interface
Inputs Processing
Transmit Data
Data Storage
Restoring Data
Digital / Analog / Pulses Signals
Measuring Equipment
Supervision System
Setting Parameters
Reading Parameters

## Slide 5
Battery
Charger
24VDC
Power Supply
Battery
Goulotte
Goulotte
Terminal Block for Detectors Connection
Electrical Cabinet
Hardware Design
SIEMENS S7-300 PLC
Ready to use up to:
8 Digital Input channels
2 Fast Counting Input channels
8 Analog Input channels
8 RS485 channels
4 Digital Dynamics Outputs

## Slide 6
Battery
Circuit Breakers
Power Supply &
Battery Charger
PLC RACK &
I/O Cards
Detectors Connections
Hardware Design

## Slide 7
Software Design
Design of a Degraded mode to increase the Buffer time

## Slide 8
Software Design
Adjustable Sampling & Buffering time range of 0.1 second to 24 days
Refresh RT Data: 1 Sampling time / Channel
Data Storage: 2 Buffering times / Channel
(1 for Measurement mode & 1 for Degraded mode)

## Slide 9
Software Design
Digital Channels
Fast Counting Channels
Analog & RS485 Channels
Events

## Slide 10
Dynamics Digital Outputs
DYNAMIC OUTPUT PARAMETERS |  | 
Name | Data Type | Comment
Flag_DI | ARRAY [1..8] of BOOL | 8 Digital Channels with 1 Alarm/Channel #1 Alarm taken into account in the equation
Flag_FC | ARRAY [1..2, 1..4] of BOOL | 2 Fast Counting Channels with 4 Alarms/Channel #1 Alarm taken into account in the equation
Flag_AI | ARRAY [1..8, 1..4] of BOOL | 8 Analog Channels with 4 Alarms/Channel #1 Alarm taken into account in the equation
Flag_RI | ARRAY [1..8, 1..4] of BOOL | 8 Remote Channels with 4 Alarms/Channel #1 Alarm taken into account in the equation
Logic_operator_1 | BOOL | #0 AND, #1 OR
Logic_operator_2 | BOOL | #0 AND, #1 OR
Timestamp | DATE_AND_TIME | Timestamp of the last configuration change
Output Equation:
(Flag_DI[1] AND DI_Channel[1].Alarm_status OR Flag_DI[2] AND DI_Channel[2].Alarm_status OR…OR Flag_DI[16] AND DI_Channel[16].Alarm_status)
[AND / OR] (Logic_operator_1)
(Flag_FC[1,1] AND FC_Channel[1].Alarm_status[1] OR Flag_ FC[1,2] AND FC _Channel[1].Alarm_status[2] OR…OR Flag_ FC[2,4] AND FC_Channel[2].Alarm_status[4]
[AND / OR] (Logic_operator_2)
Flag_AI[1,1] AND AI_Channel[1].Alarm_status[1] OR Flag_AI[1,2] AND AI_Channel[2].Alarm_status[2] OR...OR Flag_AI[8,4] AND AI_Channel[8].Alarm_status[4])

## Slide 11
Dynamics Digital Outputs
2 Dimensions Arrays: Simple Code
// Code
FOR INDEX_1:= 1 TO 8 BY 1 DO
IF DI_ALARM[INDEX_1] AND FLAG_DI[INDEX_1] = TRUE THEN // Digital Channel Alarm Synthesis
SYNTHESE_DI_ALARM:= TRUE;
END_IF;
END_FOR;
FOR INDEX_1:= 1 TO 2 BY 1 DO
FOR INDEX_2:= 1 TO 4 BY 1 DO
IF FC_ALARM[INDEX_1, INDEX_2] AND FLAG_FC[INDEX_1, INDEX_2] = TRUE THEN // Fast Counting Channel Alarm Synthesis
SYNTHESE_FC_ALARM:= TRUE;
END_IF;
END_FOR;
END_FOR;
FOR INDEX_1:= 1 TO 16 BY 1 DO
FOR INDEX_2:= 1 TO 4 BY 1 DO
IF AI_ALARM[INDEX_1, INDEX_2] AND FLAG_AI[INDEX_1, INDEX_2] = TRUE THEN // Analog Channel Alarm Synthesis
SYNTHESE_AI_ALARM:= TRUE;
END_IF;
END_FOR;
END_FOR;
IF LOGIC_OPERATOR = FALSE THEN
IF OPERATOR_2 = FALSE THEN
OUT_DO_STATUS:= SYNTHESE_DI_ALARM AND (SYNTHESE_FC_ALARM AND SYNTHESE_AI_ALARM); //Output Calculation with 2 logic operators
ELSE DO_STATUS:= (SYNTHESE_DI_ALARM AND SYNTHESE_FC_ALARM OR SYNTHESE_AI_ALARM);
END_IF;
ELSIF OPERATOR_2 = FALSE THEN
DO_STATUS:= (SYNTHESE_DI_ALARM OR SYNTHESE_FC_ALARM AND SYNTHESE_AI_ALARM);
ELSE OUT_DO_STATUS:= SYNTHESE_DI_ALARM OR SYNTHESE_FC_ALARM OR SYNTHESE_AI_ALARM;
END_IF;

## Slide 12
Application example
Hydrocarbon detector
Conventional Measurement
Radiological sampling
Pumping System
Control Command
Specific Part

## Slide 13
WATER MONITORING STATION
Pumping System
Conventional Measurement
Hydrocarbon detector
Radiological sampling
SMART INTERFACE
Application example
Ethernet
Link

## Slide 14
SCADA View

## Slide 15
Water Temperature
Rain Gauge
Data View
0
30 days

## Slide 16
Event View

## Slide 17
Manufacturing Cost:
10 K€ max.
Installation
Installation Needs:
SCADA based on the Interface Control Document

## Slide 18
Thank you for your attention
Any Questions?