## Slide 1: HL-LHC CERN 17th Dec 2015 Tunnel heat transfer estimate
M. Battistin, M. Gomez, P. Pepinster, F. Borralho

## Slide 2: Agenda
Surface measurement
Heat transfer problem
Convective heat transfer estimate
Radiation heat transfer estimate
Conclusions

## Slide 3
UL17:
SS= 153m2 S.parois= 410m2 Vol=408m3
UL13:
SS= 153m2 S.parois= 410m2 Vol=408m3
UA13:
SS= 275m2
S.parois= 632m2 Vol=1140m3
UR15:
SS= 1903m2 S.parois= 4570m2 Vol=9800m3
US17:
SS= 882m2
S.parois= 1950m2 Vol=9900m3
UA17:
SS= 275m2
S.parois= 632m2 Vol=1140m3
632 m2
410 m2
632 m2
410 m2
4570 m2
1945 m2

## Slide 4: Heat Transfer Problem
14°C
25°C
Rrock
Rconcrete
hconvection
Q???
8600 m2
Stable temperature
20 m

## Slide 5: Technical note
100 m depth -> ≈14°C

## Slide 6: Thermal Resistance Parameters
SIA Standard Soil conductivity ≈ 2.5 W m-1 K-1
SOIL
EN 12524 Concrete conductivity ≈ 2.5 W m-1 K-1
Concrete

## Slide 7: Mixed Convective Heat Transfer
Nu ≈ NuN -> the natural convection is dominating the heat transfer process
The expected heat tranfert coefficient at the wall is about 3÷15 W m-2 K-1

## Slide 8: Convective Heat Load Estimate
The maximum expected convective heat load to the ground will be 74 kW

## Slide 9: Radiation Heat Load Estimate
The radiation heat transfer is similar to the convective one
D = 3.2 m; d = 1 m
D/d ≈ 0.31 -> View Factor = 0.31
Surface = 8600 m2
T1 = 25 °C = 297 K
T2 = 14 °C = 286 K
S = 5.67*10-8 W m2 K-4
Emissivity both surfaces = 1.0
Q ≈ 80 kW

## Slide 10: Conclusions
The heat transfer between HL-LHC structure and the ground is mainly dominated by the natural convection and radiation
Considering a tunnel air temperature of 25°C…
...the expected heat load is around 150 kW

## Slide 11
Any question?