## Slide 1: Inner Triplet Magnets (MQXF) and Protection
G. Ambrosio, V. Marinozzi, E. Ravaioli, T. Salmi, E. Todesco
and the whole QXF team
Conceptual Design Review of the Magnet Circuits for the HL-LHC
March 21-23, 2016
CERN

## Slide 2: Outline
MQXF Magnets and Protection plan
Protection elements
Simulations without CLIQ
Conclusions

## Slide 3: Inner Triplet Magnets (MQXFA/B)
Operating gradient: 132.6 T/m
Coil aperture: 150 mm
Q1/Q3 magnetic length: 4.2 + 4.2 m
Q2 magnetic length: 7.15 m
Max outer diameter: 630 mm
Operating temperature: 1.9 K

## Slide 4: MQXFA/B Main Parameters
Parameter | Unit | MQXFA/B
Coil aperture | mm | 150
Magnetic length | m | 4.2/7.15
N. of layers |  | 2
N. of turns Inner-Outer layer |  | 22-28
Operation temperature | K | 1.9
Nominal gradient | T/m | 132.6
Nominal current | kA | 16.5
Peak field at nom. current | T | 11.4
Stored energy at nom. curr. | MJ/m | 1.2
Diff. inductance | mH/m | 8.2
Strand diameter | mm | 0.85
Strand number |  | 40
Cable width | mm | 18.15
Cable mid thickness | mm | 1.525
Keystone angle |  | 0.4
1st short model exceeded ultimate current at 1.9K
and 93% SSL at 4.5K

## Slide 5: Quench Protection Plan
Elements:
No Energy Extract.
CLIQ units
Heaters
Instrumentation
Strategy:
Heaters & CLIQ provide redundancy
Heaters can be optimized for low current (because there is no dump)
Some heaters may be “backup”

## Slide 6: Quench Detection
Instrumentation for Quench Detection:
4 voltage taps per coil
  2 VT per lead around Nb3Sn-NbTi splice
Detection:
Threshold: 100 mV
  at high current
Verification: 10 ms
Power supply switch:
delay: 5 ms

## Slide 7: CLIQ
Coupling-Loss Induced Quench system
  Concept and validation presented by E. Ravaioli
  Next presentation for application to Inner Triplet Circuit and failure scenarios
Note: the failure of a CLIQ unit can be simulated by single magnet analysis because of the diodes

## Slide 8: Protection Heaters
Quench heaters have been designed using copper plating for inner and outer layer:
  Two strips on each side of the outer layer
    “High Field” and “Low Field”
  One strip on each side on the inner layer
  Inner layer 40% polyimide free
Outer Layer
Inner Layer

## Slide 9: Post-test HQ02b (90 mm aperture) bore, viewed from RE
Heater bubble
Heaters on the Inner Layer may develop bubbles during operation
HQ02 quenched many times, including many High Temperature quenches
No heater failures
Porosity through the polyimide layer should reduce this problem
- Inspection in a few weeks

## Slide 10: Heaters Optimization
Heaters have been designed & optimized by
  M. Marchevsky (LBNL) design w/o copper plating
  E. Todesco (CERN) design with copper plating
  T. Salmi (Tampere Univ.) delay computation & optimizat.
    2D thermal simulation using CoHDA
    Verification & calibration using LARP HQ magnets
      Criteria adjusted from Tmax = Tcs  Tave = Tcs
HQ02a-b outer layer

## Slide 11: Protection at Low Current
Without energy extraction MQXF magnets need active protection also at low current (1 kA)
  Quench initiation in a few points per coil is enough
  Heater design can be adjusted to do it in case present heaters cannot (to be tested soon)
     Super-Heating stations

## Slide 12: Quench Protection Simulations w/o CLIQ
Hot spot computed by V. Marinozzi using QLASA
  Validation & calibration using LARP HQ and LQ magnets
  Max allowable temperature: 350 K†
    Plan to keep Hot Spot Temp < 300 K in normal condition
Peak voltages computed V. Marinozzi using ROXIE
  Used also for 11T simulations
†G. Ambrosio, “Maximum allowable temperature during quench in Nb3Sn accelerator magnets”, Yellow Report CERN-2013-006, pp. 43–46, WAMSDO 2013, CERN, Geneva, CH.
†H. Bajas, et al., “Cold Test Results of the LARP HQ02b magnet at 1.9 K”, TASC.2014.2378375

## Slide 13
Assumptions used for QLASA simulations:
Protection heaters only on the outer layer, considering super heating stations
100 mV threshold
10 ms validation time + 5 ms PS switch opening time
No energy extraction
Average heaters delay time for HF and LF zone, for normal heating stations and for super heating stations (computed by T. Salmi using CoHDA)
Longitudinal and transversal propagation taken into account
No quench propagation to the inner layer @ 1 kA
20 ms quench propagation time from outer to inner layer @ 16.47 kA
Dynamic effects on the inductance
No quench back
HF, normal HS | HF, super HS | LF, normal HS | LF, super HS
75 ms | 52 ms | 80 ms | 55 ms
OL heaters delay time @ 1 kA
HF, normal HS | HF, super HS | LF, normal HS | LF, super HS
22 ms | 20 ms | 24 ms | 22 ms
OL heaters delay time @ 16.47 kA

## Slide 14: Hot Spot Temperature (w/o CLIQ)
At 1 kA the hot spot temperature is 34 K
  If only super heating stations are considered, with 200 ms delay time (4 x computed delay time), hot spot temperature rises to 45 K
At nominal current, with only OL heaters:
  IL heaters are kept as back-up
No CLIQ No IL heaters | No CLIQ No IL heaters 1 HF strip fails | No CLIQ No IL heaters Both HF strip fail in a coil | No CLIQ No IL heaters All 4 OL strip fail in a coil
325 K | 329 K | 336 K | 347 K

## Slide 15: Peak Voltages (w/o CLIQ)
 | To ground (V) | Turn-Turn (V) | Layer-Layer (V) | Midp-Midp (V)
All heaters on | 513 | 47 | 463 | 281
Half coil OL-HF fails | 540 | 47 | 521 | 407
Half coil fail | 640 | 48 | 547 | 553
1 coil fail | 1930 | 60 | 1900 | 1790
Only OL | 757 | 86 | 560 | 350
Assumptions used for ROXIE simulations:
Magnet lenght: 7.15 m (worst case)
No energy extraction
Voltage between ends: 0 V (short circuit)
Heaters delay time from CoHDA (Tiina Salmi)
Transversal propagation considered
Inter layer propagation: 20 ms (from HQ measurem.)
Ground positioned at magnet end
No quench back

## Slide 16: Conclusions
Quench heaters protect MQXF magnets and provide redundancy to CLIQ system
Heater design can be adjusted to protect MQXF magnets at low current
  Tests will show if design adjustments are needed
Exploring option of keeping some heater strips disconnected and used as back-up
  checking voltages in failure scenarios is in progress

## Slide 17: Back up Slides

## Slide 18: CoHDA: Code for Heater Delay Analysis
Heat conduction from heater to the superconducting cable
Quench when cable reaches Tcs(I,B)
Each coil turn considered separately
  Symmetric heater geometry: Model half of the heater period
  2-D model (neglect turn-to-turn)
  Uniform magnetic field in the cable
Thermal network method
Model implementation verified in comparison with COMSOL (Thanks to Juho Rysti, CERN)
PH coverage / 2
PH period/ 2
H e a t
y, radial (in cosθ)
z, axial

## Slide 19
QLASA*
QLASA[1] is a program developed by the University of Milan and the INFN/LASA for the simulation of quench evolution in solenoids.
Main features:
Pseudo-analytical: quench propagation is based on Wilson analytical formulas[2]; thermal calculations are made solving the heat equation in adiabatic approximation.
Magnetic field is given as input
  It is possible to simulate magnetic quadrupoles or other kind of magnets
Magnet inductance is given as input
  Iron saturation can be simulated
  It is possible to simulate dynamic effects (reduction of the inductance[3])
Protection circuit with external dump resistor
It is possible to simulate protection heaters with heating stations[4]
Material properties from MATPRO[5]
[1] “QLASA: a computer code for quench simulation in adiabatic multicoil superconducting windings”, L. Rossi and M. Sorbi, 2004.
[2] “Superconducting magnets”, M.N. Wilson, 1983.
[3] “Effect of coupling currents on the dynamic inductance during fast transient in superconducting magnets”, V. Marinozzi et al., 2015.
[4] “Guidelines for the quench analysis of Nb3Sn accelerator magnets using QLASA”, V. Marinozzi, 2013.
[5] “MATPRO upgraded version 2012: a computer library of material property at cryogenic temperature,” G.Manfreda et al., 2012
*
Slides by V. Marinozzi

## Slide 20: Heater design parameters
Parameter (unit) | Value
Voltage (V) | 450
HFU capacitance (mF) | 19.2
Max. Current (A) | 200
Polyimide thickness (mm) | 0.05
Stainless steel thickness (mm) | 0.025
OL HF
OL LF
16*1.88 mm =30.0 mm : 24 mm wide heater
12*1.88 mm =22.6 mm : 18 mm wide heater
(2 turns without coverage)
(To get 150 W/cm2 and not exceed 200 A)
(Also 20 mm wide is OK.)

## Slide 21: Heater delay simulation
2-D thermal simulation using CoHDA:
2 possible criteria for quench onset
  Cable maximum temperature reaches Tcs
    -> Current redistribution starts, visible in test set-ups
  Cable average temperature reaches Tcs
    -> Current sharing with copper starts, quench propagation starts
The criterion B is more conservative, and it is used in this design and analysis.
Criterion B gives 5-10 ms longer delays

## Slide 22: The concept of Super- Heating Stations
The idea: Add a few long heating stations to make sure it quenches also at low current (as sure as possible).
Only a few HS should be enough at low current
The rest of the heater can have shorter HS with shorter period for high current quench protection
Super-HS = 2 normal lenght HS combined in every ~ 2 m
  According to my preliminary analysis (details in the appendix) this should be enough at low current (1 – 8 kA) but this needs to be confirmed by Vittorio
First generation Outer Layer heaters

## Slide 23: OL HF geometry with 5-cm-long normal HS and 10-cm-long Super-HS
Strip width = 18 mm (covers 9 turns)
Normal HS length = 5 cm (25 normal HS / strip)
Super-HS length = 10 cm (4 super-HS / strip)
Period = 25 cm (distance between the centers of heating stations)
Period for super-HS = 1.99 m
7.2 m
1.99 m
0.62 m
0.62 m
1.99 m
1.99 m
Schematic
Each distance of HS centers: 0.248 m
= 5 cm long HS
= 10 cm long HS
…
Strip R @4.5 K = 1.8 Ω
Tot R with 1 Ω margin = 2.8 Ω
I with 450 V = 157 A
Peak power = 150 W/cm2
RC τ with 19.2 mF HFU = 55 ms
SS thickness 25.4 µm, ρ = 5e-7 Ωm
Cu thickness = 10 µm, ρ = 2e-9 Ωm

## Slide 24: OL LF geometry with 6-cm-long normal HS and 12-cm-long Super-HS
Strip width = 24 mm (covers 12 turns)
Normal HS length = 6 cm (16 normal HS / strip)
Super-HS length = 12 cm (4 super-HS / strip)
Period = 36 cm (distance between the centers of heating stations)
Period for super-HS = 1.8 m
7.2 m
1.8 m
0.9 m
0.9 m
1.8 m
1.8 m
Schematic
Each distance of HS centers: 0.36 m
= 6 cm long HS
= 12 cm long HS
…
Strip R @4.5 K = 1.2 Ω
Tot R with 1 Ω margin = 2.2 Ω
I with 450 V = 202 A
Peak power = 140 W/cm2
RC τ with 19.2 mF HFU = 43 ms
SS thickness 25.4 µm, ρ = 5e-7 Ωm
Cu thickness = 10 µm, ρ = 2e-9 Ωm
Two other options for PH geom. presented in the Appendix.

## Slide 25: Simulated delays at Imag = 1 kA
B at the conductor edge (T) | HS = 5 cm (150 W/cm2) Heater delay (ms) | HS = 10 cm (150 W/cm2) Heater delay (ms) | HS = 6 cm (140 W/cm2) Heater delay (ms) | HS = 12 cm (140 W/cm2) Heater delay (ms)
0.6 (B/Bpeak = 0.8) | 69.6 | 50.6 | 73.6 | 53.6
0.6 (B/Bpeak = 0.7) | 70.3 | 51.0 | 74.5 | 54.0
0.5 (B/Bpeak = 0.6) | 78.1 | 52.1 | 85.4 | 55.2
0.4 (B/Bpeak = 0.5) | 79.1 | 52.5 | 86.9 | 55.6
0.3 (B/Bpeak = 0.4) | 80.2 | 53.0 | 88.6 | 56.2
OL HF heater, normal HS
OL HF heater, super HS
OL LF heater, normal HS
OL LF heater, super HS
Bpeak in mag. = 0.81 T
In the heater delay simulation the conductor field is taken at the edge of the conductor. This is usually the maximum field in the conductor.
For quench simulations: Associate the conductor maximum field to these delays.

## Slide 26: Simulated delays at Imag = 16.5 kA
B at the conductor edge (T) | HS = 5 cm (150 W/cm2) Heater delay (ms) | HS = 10 cm (150 W/cm2) Heater delay (ms) | HS = 6 cm (140 W/cm2) Heater delay (ms) | HS = 12 cm (140 W/cm2) Heater delay (ms)
9.1 (B/Bpeak = 0.8) | 17.0 | 16.3 | 17.0 | 16.6
8.0 (B/Bpeak = 0.7) | 19.7 | 18.7 | 19.8 | 19.2
6.8 (B/Bpeak = 0.6) | 22.7 | 21.3 | 22.8 | 21.9
5.7 (B/Bpeak = 0.5) | 26.1 | 24.1 | 26.2 | 24.8
4.6 (B/Bpeak = 0.4) | 30.0 | 27.1 | 30.2 | 28.0
OL HF heater, normal HS
OL HF heater, super HS
OL LF heater, normal HS
OL LF heater, super HS
Bpeak in mag. = 11.4 T
In the heater delay simulation the conductor field is taken at the edge of the conductor. This is usually the maximum field in the conductor.
For quench simulations: Associate the conductor maximum field to these delays.

## Slide 27: Next Steps
Heater studies during MQXFS01 test
Adjustment of CoHDA parameters (if needed)
Adjustment of heater design w SuperHeating stations
Fabrication of 2nd generation MQXF heaters

## Slide 28
Aperture diameter | 150 mm
Gradient | 132.6 T/m
Nominal current | 16470 A
Magnetic stored energy | 1.17 MJ/m
Inductance | 8.3 mH/m
Magnetic length Q1/Q3 | 2 x 4.2 m
Magnetic length Q2a/Q2b | 7.15 m
Conductor peak field | 11.4 T
Operating temperature | 1.9 K
Strand diameter | 0.850 mm
Bare cable width | 17.86 mm
Bare cable thin/thick edge thickness | 1.462/1.588 mm
Insulation thickness | 0.145 mm
Number of strands | 40
Copper/non-copper ratio | 1.2
Copper RRR | 100
1. Introduction
High stored energy
High peak field
  Protection challenging!

## Slide 29
Quench heaters have been designed using copper plating for inner and outer layer:
Two strips on each side of the outer layer (“High Field” and “Low Field”)
One strip on each side on the inner layer
  Inner layer 40% polyimide free
3. Quench heaters design