## Slide 1: Status and first results of XFEL cryogenics
Tobias Schnautz DESY MKS1
Bernd Petersen DESY MKS / XFEL WP10&13 WPL
..presenting the work of many colleagues, institutes and contractors
Notes: How to edit the title slide
Upper area: Title of your talk, max. 2 rows of the defined size (55 pt)
Lower area (subtitle): Conference/meeting/workshop, location, date, your name and affiliation, max. 4 rows of the defined size (32 pt)
Change the partner logos or add others in the last row.

## Slide 2: Overview
XFEL & XFEL cryogenic system overview
Requirements for XFEL refrigerator
Modifications of HERA cryo plant -> XFEL refrigerator
2K cold compressor system
Refrigerator commissioning & acceptance tests
Cold compressor open issues
XFEL injector cryogenic operation – first operation experience
XFEL installation status & future of cryo operation
Notes: Before you start editing the slides of your talk change to the Master Slide view:
Menu button “View” > Slide Master:
Edit the following items:
1. On the Title slide (second master slide)
a) Click to add title of your talk
b) Click to add subtitle (conference, location, name of the speaker, date)
2. On the Slide Master (first master slide)
a) The 1st row in the violet header: Delete the existent text and write the title of your talk into this text field b) The 2 rows in the footer area: Delete the text and write the information regarding your talk (same as on the Title Slide) into this text field.
If you want to use more partner logos position them left beside the DESY logo in the footer area.
Close Master View

## Slide 3: General information about XFEL - project
  Key figures:
  Length of accelerator: 1500m
  Length of facility: 3400m
  Accelerator modules : 100
  Max. electron energy: 17,5 GeV
  Max. wavelength: 0,5nm
  Start of operation: 2016

## Slide 4: Overview of XFEL Cryogenic System (1)
Warm
He-Pumps
SC
SC
SC
SC
Purifier
SC
SC
SC
SC
Purifier
Distribution Box
DB54
Cold Compressors
CB44
Distribution Box
XLVB
XRTL
(Building 54)
Cryo Plant
Distribution Box
XLVB
Shaft
Distribution Box
XLVB
FB
CM
FC
EC
3,9 GHz
Injector
Distribution Box
XIVB
FB
CM
FC
EC
3,9 GHz
AMTF
Main Linac
XLTL1
XLTL3
XLTL2
CMS
FC
EC
CMS
FC
EC
CMS
SCB
EC
CMS
FC
SCB
Linac
Contractors
LINDE
DEMACO
BINP
Coldbox 41
Coldbox 43

## Slide 5: Overview of XFEL Cryogenic System (2)
Distance: 170m
XRTL
Cold Compressor Box
CB44
Distribution Box
XLVB
Transferline to linac XLTL1
Injector
Injector boxes
XRTL
Refrigerator bldg.
XFEL XSE shaft bldg.

## Slide 6: Overview of XFEL Cryogenic System (3)
Contributions from Budker Institute for Nuclear Physics (BINP),
Novosibirsk, Russia
XFEL Injector valve boxes XIVB &FB
XFEL Injector transfer lines, feed- & end caps
Distribution valve box XLVB
All equipment delivered, installed and in use already (XFEL injector)
(XLVB warm gas tubing will be modified)

## Slide 7: Overview of XFEL Cryogenic System (4)
DeMaCo Netherlands supplied:
Transfer-lines: XRTL; XLTL1..3
String-Connection-Boxes 1-6
Feed-Caps 1-3
End-Caps 1-3
all equipment delivered & installed(*)
XRTL
XLTL1
Feed-Cap 1 at DeMaCo / in XFEL tunnel
(*) XLTL1 not yet connected to XLVB by intention

## Slide 8: Requirements on XFEL Refrigerator (1)
Requirements on XFEL refrigerating plant (17.5 GeV)
2K: 1.9 kW (incl. 30% overcapacity)
5/8K: 3.6 kW (incl. 50% overcapacity)
40/80K: 24 kW (incl. 50% overcapacity)
Operation: 24 h/d, 7 d/week
Run periods of 2-3 years without scheduled break
Refrigerator availability > 99%
Cold Compressor suction pressure stability < 1%
‚TESLA-Technology‘
1.3 GHz superconducting cavities
XFEL cryomodule = 8 cavities + 1 sc quad

## Slide 9: Requirements on XFEL Refrigerator (2)
Industrial Study (LINDEKRYOTECHNIK,2006) and its Results:
  2 HERA refrigerators (subplants) + 2K system (cold compressors) could be modified to XFEL-refrigerator
Use of existing HERA helium refrigerator = cheapest solution
-> reason to realize this solution
LINDEKRYOTECHNIK (LKT) contractor for XFEL refrigerator

## Slide 10: Requirements on XFEL Refrigerator (3)
DESY 17.5 GeV specification
2K: 1.46 (+30% = 1,9) kW
5K–8K: 2.4 (+50% = 3.6) kW
40K-80K: 16.0 (+50% =24) kW
Hope: operating 17.5 GeV Linac with one refrigerator (CB) should be possible and would save primary energy costs
LKT prognosis for one coldbox:
2K: 2.01 kW
5K-8K: 3.03 kW
40K-80K: 20.17 kW
‚One Cold-Box‘ Option ???

## Slide 11: Modifications of the refrigerator Coldboxes The effect from 4.5K to 2K…
Modifications
50% of all piping were modified
LN2 precooling heatexchanger was removed
Turbines were re-arranged and equipped with optimised flow parts
At least some items remained
Platefin heatexchangers
80K and 20K Adsorber
Cryogenic valves (shaft, stem and some plugs)
17 years of operational experience  automated procedures migrated into plc

## Slide 12: HERA Refrigerating Plant XFEL Refrigerating Plant Overhauling, modifications, extensions
To be modified
To be removed
No changes
LN2 heat exchanger removed
Re-arrangement of turbine strings
50% of piping modified

## Slide 13: Overhaul of the Compressor System Facts & figures
Main Objective
To ensure «a sufficient helium-supply of the XFEL-linac for at least 15 years of continuous operation» [from T. Schnautz, B. Petersen «Specification of the XFEL-Refrigerator»]
Some numbers about overhauling:
Adsobent replacement at 4 dryers
Revision of 9 screw compressor blocks
Calibration of 178 safety valves
New sealings at 1292 manual valves
Painting of all equipment overhauled
Pressure & leak test

## Slide 14: HERA Refrigerating Plant XFEL Refrigerating Plant Overhauling, modifications, extensions
Contributions
LINDE
SC
SC
SC
SC
Purifier
SC
SC
SC
SC
Purifier
Distribution Box
DB54
Coldbox 41
Coldbox 43

## Slide 15: HERA Refrigerating Plant XFEL Refrigerating Plant Overhauling, modifications, extensions
SC
SC
SC
SC
Purifier
SC
SC
SC
SC
Purifier
Distribution Box
DB54
Cold Compressors
CB44
Distribution Box
XLVB
XRTL
Coldbox 41
Coldbox 43
CB44: Four cold compressors with a compression ratio of > 45/1

## Slide 16: Cold Compressors Cold Compressor Bypass Operation
x %
x %
(100-x) %
2K Return
2K Return
Cold Compressor Box CB44
4 cold compressors, total compression ratio = 1/45.8
Full flow re-cooling bypass
Startup & pumpdown independent from «experiment side»
Re-connection to sub-atmospheric linac (demonstrated for injector)
Operational robustness due to high internal turndown ratio
CC kept in operating map
Remark:
internal bypass is a great help for operation -
but it is no energy saver !

## Slide 17: Screen Shot from CSS Applications SDS (Synoptic Display Studio)

## Slide 18: Refrigerator commissioning & acceptance tests (1)
SC
SC
SC
SC
Purifier
SC
SC
SC
SC
Purifier
Distribution Box
DB54
Cold Compressors
CB44
Distribution Box
XLVB
XRTL
Distribution Box
XLVB
Shaft
(Building 54)
Cryo Plant
Coldbox 41
Coldbox 43
Testbox 44
Performance tests:
1. Single coldbox operation: CB41 or CB43 with cold compressors (CB44)
2. Parallel coldbox operation: CB41 and CB43 with cold compressors (CB44)

## Slide 19: Refrigerator commissioning & acceptance tests (2)
  Parallel CB operation demonstrated
  Capacity tests for single & parallel CB operation
  Specified capacities exceeded for parallel CB operation
  Single CB operation -> seems to be sufficient for XFEL linac operation
  ‚mixed-cycle‘ operation of CCs demonstrated (25% dynamic range)
 | CC mass flow [g/s] | CC inlet pressure [mbar] | CC discharge pressure [mbar] | 5-8K [kW] | 40-80K [kW]
XFEL spec (no margin) | 74 | 24 | 1100 | 2.4 | 16
Single ColdBox CB41 | 99.6 | 22.9 | 1100 | 2.74 | 18.14
Single Coldbox CB43 | 102.7 | 21.8 | 1100 | 2.78 | 18.06
Single Coldbox operation CB43 CCs Part Load ‚mixed-cycle‘ | 75 | 23.3 | 815 | 3.15 | 20
Parallel-operation measured (at design spec) | 106.6 | 23.2 | 1100 | 4 | 26.7
Capacity shifted from 2K to 5K
Notes: Before you start editing the slides of your talk change to the Master Slide view: Menu button “View”, Master, Slide Master:
Edit the following 2 items in the 1st slide: 1) 1st row in the violet header: Delete the existent text and write the title of your talk into this text field 2) The 2 rows in the footer area: Delete the text and write the information regarding your talk (same as on the Title Slide) into this text field.
If you want to use more partner logos position them left beside the DESY logo in the footer area Close Master View

## Slide 20: Refrigerator commissioning & acceptance tests (3)
  2K operation pressure stability better +/- 1% demonstrated
Chart: CC Inlet Pressure
Plot from single cold box operation of CB41
Notes: Before you start editing the slides of your talk change to the Master Slide view: Menu button “View”, Master, Slide Master:
Edit the following 2 items in the 1st slide: 1) 1st row in the violet header: Delete the existent text and write the title of your talk into this text field 2) The 2 rows in the footer area: Delete the text and write the information regarding your talk (same as on the Title Slide) into this text field.
If you want to use more partner logos position them left beside the DESY logo in the footer area Close Master View

## Slide 21
… we are in quite good shape – but there are some poblems to be solved:
Bearing failures at cold compressors (ceramic bearings)
Cold compressor stage | Current Pressure ratio [mbar] | Bearing failures | Expected lifetime [h] Scheduled / expectation | Observed very preliminary [h]
CC-stage 1 (44CC1211) | 26 / 118 | No failures | 16000 /16000 | open
CC-stage 2 (44CC1212) | 118 / 330 | 4 | 16000/30000 | 286
CC-stage 3 (44CC1213) | 330 / 815 | 4 | 16000/32000 | 288
CC-stage 4 (44CC1214) | 815 / 1090 | 1 | 16000/41000 | open
LINDEKRYOTECHNIK started root cause analysis
General analysis is conducted: frequency spectra monitoring, general review of loads ..etc.etc.
Some construction changes are already implemented
Test bench will be installed
800h continous operation to be demonstrated
…list of open issues after final acceptance
C
Commissioning – open issues

## Slide 22: XFEL-Injector-Operation (1)
SC
SC
SC
SC
Purifier
SC
SC
SC
SC
Purifier
Distribution Box
DB54
Cold Compressors
CB44
Distribution Box
XLVB
XRTL
(Building 54)
Cryo Plant
Distribution Box
XLVB
Shaft
Distribution Box
XLVB
FB
CM
FC
EC
3,9 GHz
Injector
Distribution Box
XIVB
FB
CM
FC
EC
3,9 GHz
AMTF
Warm
He-Pumps
Linac
Coldbox 41
Coldbox 43
Cool-down December 2015
operated continously until now
scheduled warm-up end July 2016

## Slide 23: XFEL Injector Operation (2)
XFEL Injector in operation since December 2015
First beam 2 weeks after cool down – before Christmas !!
Status June 2016:
XFEL design emittance demonstrated

## Slide 24: XFEL installation status
XM 4
L2
L1
XM 5
XM 1
XM 2
XM -1
L3
L3
L3
L3
L3
L001
A2.1.L1
BC1
L2
L3
L3
BC2
XM 7
XM 6
XM11
XM 3
XM 13
XM 9
XM 10
XM 19
L002
A2.2.L1
L003
A2.3.L1
L004
A2.4.L1
L005
A3.1.L2
L006
A3.2.L2
L007
A3.3.L2
L008
A3.4.L2
L009
A4.1.L2
L010
A4.2.L2
L011
A4.3.L2
L012
A4.4.L2
L013
A5.1.L2
L014
A5.2.L2
L015
A5.3.L2
L016
A5.4.L2
L017
A6.1.L3
L018
A6.2.L3
L019
A6.3.L3
L020
A6.4.L3
L021
A7.1.L3
L022
A7.2.L3
L023
A7.3.L3
L024
A7.4.L3
L025
A8.1.L3
L026
A8.2.L3
L027
A8.3.L3
L028
A8.4.L3
L029
A9.1.L3
L030
A9.2.L3
L031
A9.3.L3
L032
A9.4.L3
L033
A10.1.L3
L034
A10.2.L3
L035
A10.3.L3
L036
A10.4.L3
L037
A11.1.L3
L039
A11.3.L3
L040
A11.4.L3
L041
A12.1.L3
L042
A12.2.L3
L043
A12.3.L3
L044
A12.4.L3
L045
A13.1.L3
L046
A13.2.L3
L047
A13.3.L3
L048
A13.4.L3
L049
A14.1.L3
L050
A14.2.L3
L051
A14.3.L3
L052
A14.4.L3
L053
A15.1.L3
L054
A15.2.L3
L055
A15.3.L3
L056
A15.4.L3
L057
A16.1.L3
L058
A16.2.L3
L059
A16.3.L3
L060
A16.4.L3
L061
A17.1.L3
L062
A17.2.L3
L063
A17.3.L3
L064
A17.4.L3
L065
A18.1.L3
L066
A18.2.L3
L067
A18.3.L3
L068
A18.4.L3
L069
A19.1.L3
L070
A19.2.L3
L071
A19.3.L3
L072
A19.4.L3
L077
A21.1.L3
L078
A21.2.L3
L079
A21.3.L3
L080
A21.4.L3
L089
A24.1.L3
L090
A24.2.L3
L091
A24.3.L3
L092
A24.4.L3
L081
A22.1.L3
L082
A22.2.L3
L083
A22.3.L3
L084
A22.4.L3
L093
A25.1.L3
L094
A25.2.L3
L095
A25.3.L3
L096
A25.4.L3
L073
A20.1.L3
L074
A20.2.L3
L075
A20.3.L3
L076
A20.4.L3
L085
A23.1.L3
L086
A23.2.L3
L087
A23.3.L3
L088
A23.4.L3
L097
A26.1.L3
L098
A26.2.L3
L099
A26.3.L3
L100
A26.4.L3
L038
A11.2.L3
XM 18
DEMACO Cryo-connection
TMPL
DACHS
door
1.508 m
2.130 m
Hitch for hanging machine
XM 27
XM 20
A2
A6
XM 30
A7
A8
XM 31
XM 28
XM 14
XM 34
P
XM 26
XM 35
XM 37
SCB 1
DEMACO Cryo-connection
XM 38
SCB 2
XM 39
XM 40
XM 41
XM 36
XM 43
XM42
XM47
XM44
P
P
XM 49
XM 16
XM 33
XM 45
XM 15
A9
A10
52
53
54
55
56
57
58
59
61
60
62
63
XM 51
XM 17
XM55
XM 52
XM 53
XM 25
A11
A12
A13
A14
XM 32
XM 67
P
XM 56
P
P
XM 48
XM 23
XM 58
x
x
x
50
XM59
XM 12
P
P
P
Container for condensed water
250 ltr.
SCB 4
XM65
68
67
70
74
73
72
71
75
69
66
64
76
XM 64
XM 60
SCB 3
XM 57
XM 71
UV XTL-2AV
XM 63
XM 66
51
XM 21
XM 61
XM 69
XM 68
XM 70
A5
A15
A16
A17
XM 72
XM 73
XM 76
XM 62
A4
A3
x
x
x
x
x
x
P
P
P
P
CS1
CS2
CS2
CS3
CS4
CS5
CS6
CS7
CS8
CS9
Cryo stage
65
32
79
78
77
80
81
82
83
84
85
86
87
88
89
Cryo stage
XM -2
XM 74
XM 77
SCB 5
P
Cryo stage
XM 79
Cryo stage
P
P
P
CR
CR
P
P
Cryo stage
Cryo stage
Support
XM 81
XM 80
XM 78
XM 75
CR
Cryo stage
Cryo stage
Container for condensed water
300 ltr.
Cryo stage
90
91
93
94
100
Status 03.06.2016
76 Modules installed 1 RF-Station ready
+ 8 in preparation now 6 RF-Stations under commissioning
9 RF-Station in preparation

## Slide 25: Summary & Future Plans
XFEL cryo system: installation completed (99%)
Refrigerator capacities: specification exceeded
2K CC operation: main features demonstrated
2K CC issues: bearings – problems to be solved
Continous operation of XFEL injector demonstrated
Future plans:
Cryomodule installation completed/ tunnel closed 9/2016
XFEL linac cool down: procedures will start October 4, 2016, 8:00h
First beam in XFEL linac before Christmas 2016
Thank you for yor attention !