## Slide 1
Replacement of RD1/RD34 power converters for increased rejection of network perturbations
Hugues Thiesen
  LHC-MPP Meeting
  March, 4th 2016
Acknowledgements: M. Zerlauth, I. Romera Ramirez, G. Le Godec, I. Josifovic

## Slide 2: AC network perturbations
Perturbations are < 100 ms and < 15%:
2011

## Slide 3: RPTG power converter
∆I /I = 0.3 A/ 335 A = 8.95 E-4
(FMCM threshold = 3.5 E-4)
FMCM: RD1.LR1 27/07/2011 at 06:03
E = 3.5 TeV
Today most sensitive circuits are supplied RPTG power converters
20 ms between 2 points
10V
0.3A
335.35A
I_ref and I_out
V_ref and V_out
1s
1s

## Slide 4: New RPTG power converter
Current RPTG Thyristor Power Converters
New RPTG
Switch Mode Power Converters (Based on B8 Type)
Main characteristics:
Max Output voltage: 700V
Max Output current: 810A
Max RMS current: 810A
Output Power: 567kW
Input voltage: 3x18kV/50Hz
Main characteristics:
Max Output voltage: 950V
Max Output current: 810A
Max RMS current: 810A
Output Power: 769.5kW
Input voltage: 3x18kV/50Hz

## Slide 5: New RPTG power converter
New RPTG
Switch Mode Power Converters (Based on B8 Type)
Main characteristics:
Max Output voltage: 700V
Max Output current: 810A
Max RMS current: 810A
Output Power: 567kW
Input voltage: 3x18kV/50Hz
FWD
CB
or

## Slide 6: New RPTG power converter
New RPTG
Switch Mode Power Converters (Based on B8 Type)
Main characteristics:
Max Output voltage: 700V
Max Output current: 810A
Max RMS current: 810A
Output Power: 567kW
Input voltage: 3x18kV/50Hz
frequency [Hz]
Amplitude [dBµV]
92 [40mVrms]
101 [110mVrms]
78 [8mVrms]
66 [2mVrms]
60 [1mVrms]
50Hz
10kHz
150kHz
500kHz
--- 1 mA peak-peak constraint
--- Output voltage ripple constraint

## Slide 7: Installation
18kV TRAS
CVS
18kV TRAS
CVS
Interface Rack
Switch 18kV
Old_RPTG
New_RPTG

## Slide 8: Installation
FMCM
WIC
EIS
CCC
EL
Interfaces with the safety systems

## Slide 9: Planning
LS1
18 kV switch
2016
Production of the load switches abd power converters
EYTS
Installation and commissioning