## Slide 2
Mirko Pojer and Matteo Solfaroli
Powering tests preparation_meeting 12

## Slide 3: Cryogenics
Beam screen conditioning test done in
  S12, S34, S45, S81
  S56 and S67 could be done from Friday night
  S23 and S78 to be possibly done during
  the week-end
“maximum heat load” test ongoing
  S78 to be completed – conditions back this evening/tomorrow morning
  S23 will be completed tomorrow
2 days will be needed at the end to set S23 and S78 in Run II configuration

## Slide 4: Summary status
Circuit type | Completion [%]
RBs | 97% (all done – 2 signatures missing)
RQs | 89% (all done – repeated, sign.missing)
ITs | 100%
IPQs | 99%
IPDs | 100%
600 A | 98%
120-60 A | 99% (just 1 x60 A in S34)
Total | 98% (8479 oo 8592 successful tests)
A couple of QPS/EE issues (detailed list below)
PID parameters for the IT correctors to be improved

## Slide 5: Status of RB circuits
RB.A12 OK
RB.A23 OK (1 quench @11040 A (C24R2=2195, 1st quench))
RB.A34 OK
RB.A45 OK
RB.A56 quenched at 11076 A (B33R5=3375, quenched in 2008), then reached 11080 A – fuse changed, tests ongoing
RB.A67 OK
RB.A78 OK
RB.A81 OK

## Slide 6: RB FPA at 2 kA on the ramp
FPA at 2 kA on the ramp was asked by EPC, to check the oscillation dumping system of the PC output filter; done on
  RB.A12
  RB.A23
  RB.A34
  RB.A45
  RB.A56
  RB.A67
  RB.A81

## Slide 7: RQD/F tested with new current
RQD/F.A12 – last step done with new values
RQD/F.A23 – last step done with new values
RQD/F.A34 – last step done with new values
RQD/F.A45 – last step done with new values
RQD/F.A56 – last step done with new values
RQD/F.A67 – last step done with new values
RQD/F.A78 – as soon as cryo is available
RQD/F.A81 – last step done with new values
Tests repeated also to re-measure some busbar segments with slightly higher resistance; pyramid also requested on S23 and S78 (to be done after cryo recovery)

## Slide 8
The last test did not trigger the scope acquisition, so after discussing with Mateusz we propose to continue like this:
4) Repeat the 2 kA, 10 A/s test (with new triggering condition)
5) 5 kA, 10 A/s test
6) I_nom+100 A, 0 A/s
7) 10.5 kA, 10 A/s
Once all tests are finished, and the results are correct, then it would be very nice if we could move the scope to one of the RQD/F.A56 circuits so that we also get references curves for the RQ. This of course depends on available time.
If possible, I would propose to do the following tests:
760 A, 0 A/s, 1 A fuse
2 kA, 0 A/s, 1 A fuse
5 kA, 0 A/s, 1 A fuse
I_nom, 0 A/s, 1 A fuse
5 kA, 0 A/s, 200 mA fuse
I_nom, 0 A/s, 200 mA fuse
The resistance of a 200 mA fuse (about 17 Ohm ?) is quite a bit higher than the one of a 1 A fuse (1 Ohm) and therefore strongly affects the earth current (as we already noticed on the PM file of the RB.A56 quench).
After the last test we leave the 200 mA fuse in the RQ circuit (while the RB.A56 will keep the 1 A fuse in).
Cheers,
Arjan

## Slide 9: S12
Missing in A12
  RQT13.R1B1: Noise in U_HTS – acceptable for QPS…
  RQTL11.R1B1 and B2: trip on STRONG 0V crossing Jens working on them

## Slide 10: S23
Missing in XR2
  RCBXH2.R2 – last test done
Precycles performed on available circuits
No cryo conditions

## Slide 11: S34
Missing in A34
  RCBV13.L4B2
    resistance is double the maximum: Giorgio cleaned the contacts, the connection was changed, but still not good.
  RQD.A34 CL T badly regulated
  Repetition of series of manual ramps on RCD.A34B1 completed, as requested by MP3+EPC. The circuit completed all the additional tests without trips.
Missing in ML4
  RU.L4 – PNO.a3 done; not signed due to “some high U_res value” – not possible to optimize further

## Slide 12: S34

## Slide 13: S45
Fully commissioned

## Slide 14: S56
Missing in XR5
  RCBXH1.R5 – still problem of lead cooling
Missing in LR5
  RQ4.R5 – completed, but problem in lead T regulation
  RQ5.R5 – completed, but problem in lead T regulation
Missing in A56
  RB.A56 – reached 11080 A; series of tests ongoing
    Repeat the 2 kA, 10 A/s test (with new triggering condition)
    5 kA, 10 A/s test
    I_nom+100 A, 0 A/s
    10.5 kA, 10 A/s – to be done today

## Slide 15: S67
Missing in A67
  ROD.A67B1 – tripping at 120 A; nDQQDG A wrong firmware one U_res not moving, the other going to saturation
  RQTL10.L7B1 – trip at 56 A, nDQQDG A wrong firmware ongoing
  RSS.A67B2 – 0V crossing trip
  RQ6.L7B1/2 completed by reducing ramp rate to 0.75 A/s (from 1.2 A/s)

## Slide 16: S78
Missing in A78
  RQS.A78B2
  RSS.A78B2
  ROF.A78B2 tripping at 56 A “current leads swapped”
  RQTL9/10.R7B1/2 – problem with the reset of the board; wrong firmware
  RQ6.R7B1/B2 – Jens working on it (blocked till further notice)
  RQTL7.R7B2 – 0V crossing trip
  RQTL8.R7B2 – quench
  RQT13.R7B1
  RQT12.R7B1 – trip at 57 A; nDQQDG A wrong firmware
  RQTL11.R7B1
No cryo conditions

## Slide 17: S81
Missing in A81
  RQTL11.L1B1 – 0V crossing
Precycle performed on available circuits

## Slide 18: Accesses
Thu. 17th March, 19h-21h: commissioning of the smoke detection of UXC55 (no personnel underground as the evacuation sirens will ring in all underground areas, LHC tunnel and CMS caverns)