## Slide 1: Comparison of magnet designs from a circuit-protection point-of-view
Arjan Verweij, M. Prioli, CERN, TE-MPE
A. Verweij, EuroCirCol review 11-13 May 2016

## Slide 2: Reminder
Sept 2008: damage caused in the LHC by 0.6 GJ stored energy
The stored energy of all main dipoles in the FCC is about 200 GJ.
 Circuit protection is extremely important
A. Verweij, EuroCirCol review 11-13 May 2016

## Slide 3: Intro
The FCC main dipole magnets have to be powered in strings, so:
the magnet design has an impact on the protection and configuration of the string,
the string layout has an impact on the magnet requirements.
A. Verweij, EuroCirCol review 11-13 May 2016
The following magnet designs are compared from a circuit protection point of view:
  Cos-, INFN, EuroCirCol collaboration
  Block, CEA, EuroCirCol collaboration
  Common coil, CIEMAT, EuroCirCol collaboration
  Block, LBNL
Quench protection of the magnet itself (characterised by the hot-spot temperature, voltage-to-ground, thermal gradients) is not discussed here.
(see presention T. Salmi).

## Slide 4: Recap: Powering of the LHC dipole circuits
The 154 twin-aperture magnets in each of the 8 sectors of the LHC are powered in series and each magnet has a bypass diode to decouple the current decay of a quenching magnet from the current decay of the circuit.
Ramp up and down, assuming constant ramp rate:
Output voltage of the converter: VPC=L(I)*(dI/dt) + I*Rwarm
Power of the converter: PPC=VPC*I=L(dI/dt)*I + I2*Rwarm
Ramp time: tramp=Inom/(dI/dt)
Two room-temperature energy-extraction (EE) systems, each with a switch and a 75 mW resistor (REE) are present, to ensure a sufficiently fast decay of the circuit current (t=100 s) in case of a Fast Power Abort (FPA) triggered by a quench/trip.
Diodes and (possibly non-SC) busbars therefore have to withstand this current decay.
PC
A. Verweij, EuroCirCol review 11-13 May 2016

## Slide 5: Quench/trip  Fast Power Abort (FPA)
the power converter is switched off,
the switches of the EE system(s) are opened,
quench heaters (or CLIQ) are activated,
the current in the quenching magnet(s) transfers into the bypass diode,
the voltage over the quenching magnet(s) equals the forward voltage of the bypass diode,
the circuit current decays ‘exponentially’ with tcirc=Lcirc/(NEE*REE),
magnets
EE
magnets
EE
IREE/2
0
-IREE/2
Vgnd
A. Verweij, EuroCirCol review 11-13 May 2016

## Slide 6: Required voltage withstand level
For a circuit with grounding in the centre of the EE resistor, the maximum voltage-to-ground without faults equals:
Vgnd,max = VQ,max + VFPA,max = VQ,max + 0.5*I*REE
VQ,max is given by the layout of the coils and magnet protection system.
(see presentation T. Salmi)
Fault scenario’s (for a circuit with one or two EE systems):
Malfunctioning of part of the magnet protection can give an increased VQ,max.
An intermittent short (before the circuit fuse blows) could give:
VFPA,max,fault = I*REE + Nmag*Vdiode /NEE (private comm. E. Ravaioli)
Nmag: the number of magnets in the circuit
Vdiode: the opening voltage of the cold bypass diode (6 V).
A safe voltage withstand level of the circuit is:
VWL = f * (VQ,max + VFPA,max,fault) with f a safety margin (for example f=1.2)
A. Verweij, EuroCirCol review 11-13 May 2016

## Slide 7: Powering of the FCC dipole circuits
An “LHC-type” powering seems also for the FCC the best configuration.
A. Verweij, EuroCirCol review 11-13 May 2016
However, some modifications could be envisaged:
Independent powering of the two apertures.
Powering of dipoles and quadrupoles in series.
More than one circuit per sector.
Different number of EE systems per circuit.
Cold EE systems.
Cold EE switches (persistent mode).
More than one diode per magnet.
The diode by-pass should preferably also cover the magnet-to-magnet busbar to avoid a ‘2008-like accident’.

## Slide 8: Circuit configuration
In general it is preferable to reduce the number of circuits  less power converters, warm busbars, electrical Distribution Feed Boxes (DFB), and current leads.
For a circuit, one would like to reduce:
current in the circuit → smaller size DFB & current leads, lower cost PC
VPC and PPC → lower cost and smaller size of the converter
ramping time → increased availability for beam physics
VFPA,max → reduced voltage withstand level
tcirc → faster cryo recovery, less quench propagation
dimensions cold busbars → ‘easier’ layout inside the cryostats
number of EE systems → lower cost, less maintenance, lower heat inleak
current rating of EE systems → lower cost, smaller size
stored energy per circuit → reduced risk in fault scenario’s
heating in the bypass diode → smaller diode heat sinks, faster cryo recovery
And of course, the EE systems and PC’s should be located in easily accessible areas.
Unfortunately, many of these demands are contradictory...
A. Verweij, EuroCirCol review 11-13 May 2016

## Slide 9: The FCC layout
PC 1
PC 2
Powering Sectors (4 km)
Half-arc
(8 km)
In total 20 Powering Sectors:
16 in the arcs
4 in the mini-arcs
A. Verweij, EuroCirCol review 11-13 May 2016

## Slide 10: Strategy for circuit configuration
Locate power converters and EE systems in the access points.
Subdivide each Powering Sector in N circuits  20N circuits for the entire machine
Power both apertures of the dipoles in series, independently from the quads.
Power the circuits via a superconducting link.
Use one EE system per circuit, located near the converter.
Powering Sector (4 km)
PC 1a
EE1a
PC 1b
EE1b
PC 1c
EE1c
PC 1d
EE1d
PC 1e
EE1e
Superconducting link
Example for N=5
A. Verweij, EuroCirCol review 11-13 May 2016

## Slide 11: FCC magnet designs
Block
Block (LBNL)
Cos-
Common coil
A. Verweij, EuroCirCol review 11-13 May 2016

## Slide 12: FCC magnet designs (Bnom=16 T, 14.3 m)
Description | Cos- [1] | Block [2] | Common Coil [3] | Block - LBNL [4] | Units
Nr of turns per aperture | 230 | 306 | 394 [5] | 92 | -
Current @ nominal field | 10.275 | 8.47 | 9.03 | 25.8 | [kA]
Inductance (double aperture) | 734 | 1264 | 1824 | 120 | [mH]
Stored energy at nominal (double aperture) | 39 | 45 | 74 | 40 | [MJ]
[1] G. Bellomo, P. Fabbricatore, S. Farinon, V. Marinozzi, M. Sorbi, G. Volpini, INFN, Version 28b-38 v5, Minutes EuroCirCol WP 5 meetings.
[2] C. Lorin, M. Dunante, CEA/IRFU, Version v26cmag, Minutes EuroCirCol WP 5 meetings
[3] T. Martinez, J. Munilla, F. Toral, CIEMAT, Version v1h_intgrad, Minutes EuroCirCol WP 5 meetings.
[4] G.L. Sabbi et al, “Design study of a 16 T Block-Dipole for FCC”, EUCAS 2015.
[5] Total for a double aperture divided by 2
50 mm aperture
~82% on loadline at 1.9 K
Jc=1500 A/mm2 at 16 T, 4.2 K
60 mm aperture
90% on loadline at 1.9 K
Jc=1500 A/mm2 at 16 T, 4.2 K
A. Verweij, EuroCirCol review 11-13 May 2016

## Slide 13: Assuming 2x larger stored energy with same current
 | Circuit powering
Lcirc | 2x larger
VPC | 2x larger
PPC | 2x larger
Awarm-leads | equal
Acurrent-leads | equal
 | Magnet protection
LM | 2x larger
MIIts | larger
VQ,max | larger
Thot | larger
Same:
cable
circuit
ramp time
nr of EE systems (NEE)
VFPA,max
 | Circuit protection
Ecirc | 2x larger
tcirc | 2x larger
Abusbar | 2x larger
Qdiode | 2x larger
EE switch | equal
EE dump | 2x larger
 More copper in cable
 Increase nr of circuits or number of EE systems
High priority: Minimize stored energy
A. Verweij, EuroCirCol review 11-13 May 2016

## Slide 14: Stored energy vs. Cost and Availability
Two remarks:
Assuming 200 GJ (about 40 MJ/magnet) and a ramp time of 20 min, requires an average power consumption during ramping of 170 MW (+losses due to converter efficiency and warm busbars). Increasing the stored energy has a huge cost! Reducing the ramp time has a large impact on availability. (Ramping up/down in the LHC takes a few hrs per day)
Cryo recovery after a LHC dipole quench (7 MJ/magnet) takes about 10 hours. Any further increase in stored energy for the FCC will increase the cost for the cryogenic system or increase down-time of the machine.
A. Verweij, EuroCirCol review 11-13 May 2016

## Slide 15: Assuming 2x larger cable (half number of turns) with same stored energy
 | Magnet protection
LM | 4x smaller
MIIts | 4x larger
VQ,max | ~2x smaller
Thot | equal
 | Circuit powering
Inom | 2x larger
Lcirc | 4x smaller
VPC | 2x smaller
PPC | equal
Awarm-leads | larger
Acurrent-leads | larger
 | Circuit protection
Ecirc | equal
tcirc | 2x smaller
Abusbar | 2x larger
Qdiode | equal
EE switch | 2x higher current rating
EE dump | equal
Same:
circuit
ramp time
nr of EE systems (NEE)
VFPA,max
Not obvious what is preferable:
Low-Inom & High-LM versus High-Inom & Low-LM
A. Verweij, EuroCirCol review 11-13 May 2016

## Slide 16: Are there hard limits for the magnet design?
Magnet powering:
Trade-off between: Number of circuits
Converter voltage rating (VPC)
Ramp time (tramp)
Circuit protection
Trade-off between: Number of circuits
tcirc (busbar & diode size & quench propagation)
VFPA,max
A string of magnets can always be protected, for any magnet design and given constraints (voltage withstand level, tcirc, …), by adapting the number of circuits, so by subdividing a powering sector in multiple circuits.
A. Verweij, EuroCirCol review 11-13 May 2016

## Slide 17: Layouts for the EuroCirCol Cos- design
Nr of circuits per half-arc | 1 | 2 | 3 | 4 | 4 | 8
Nr of circuits entire FCC | 20 | 40 | 60 | 80 | 80 | 160
Magnets per circuit | 215 | 113 | 72 | 54 | 54 | 27
Inductance per circuit [H] | 158 | 79 | 53 | 39 | 39 | 20
Stored energy per circuit [GJ] | 8.3 | 4.2 | 2.8 | 2.1 | 2.1 | 1.1
Ramp time [min] | 20 | 20 | 20 | 20 | 20 | 20
VPC [V] | 1350 | 676 | 450 | 338 | 338 | 169
VFPA,max [kV] | 1 | 1 | 1 | 1 | 0.5 | 0.5
VFPA,max,fault [kV] | 3.3 | 2.6 | 2.4 | 2.3 | 1.3 | 1.2
tcirc [s] | 810 | 405 | 270 | 203 | 405 | 203
Abusbar [mm2] | 539 | 387 | 316 | 273 | 387 | 273
Qdiode [MJ] | 8.3 | 4.2 | 2.8 | 2.1 | 4.2 | 2.1
A. Verweij, EuroCirCol review 11-13 May 2016
A. Verweij, EuroCirCol review 11-13 May 2016

## Slide 18: Layouts for the EuroCirCol Block design
Nr of circuits per half-arc | 1 | 2 | 4 | 6 | 6 | 12
Nr of circuits entire FCC | 20 | 40 | 80 | 120 | 120 | 240
Magnets per circuit | 215 | 108 | 54 | 36 | 36 | 18
Inductance per circuit [H] | 272 | 136 | 68 | 45 | 45 | 23
Stored energy per circuit [GJ] | 9.7 | 4.9 | 2.4 | 1.6 | 1.6 | 0.8
Ramp time [min] | 20 | 20 | 20 | 20 | 20 | 20
VPC [V] | 1920 | 960 | 480 | 320 | 320 | 160
VFPA,max [kV] | 1 | 1 | 1 | 1 | 0.5 | 0.5
VFPA,max,fault [kV] | 3.3 | 2.6 | 2.3 | 2.2 | 1.2 | 1.1
tcirc [s] | 1150 | 575 | 288 | 192 | 384 | 192
Abusbar [mm2] | 538 | 380 | 269 | 220 | 310 | 220
Qdiode [MJ] | 9.7 | 4.9 | 2.4 | 1.6 | 3.2 | 1.6
A. Verweij, EuroCirCol review 11-13 May 2016

## Slide 19: Layouts for the EuroCirCol Common coil design
Nr of circuits per half-arc | 1 | 4 | 6 | 8 | 8 | 12
Nr of circuits entire FCC | 20 | 80 | 120 | 160 | 160 | 240
Magnets per circuit | 215 | 54 | 36 | 27 | 27 | 18
Inductance per circuit [H] | 392 | 98 | 65 | 49 | 49 | 33
Stored energy per circuit [GJ] | 16 | 4 | 2.7 | 2 | 2 | 1.3
Ramp time [min] | 20 | 20 | 20 | 20 | 20 | 20
VPC [V] | 2950 | 740 | 492 | 370 | 370 | 246
VFPA,max [kV] | 1 | 1 | 1 | 1 | 0.5 | 0.5
VFPA,max,fault [kV] | 3.3 | 2.3 | 2.2 | 2.2 | 1.2 | 1.1
tcirc [s] | 1770 | 443 | 295 | 221 | 443 | 295
Abusbar [mm2] | 710 | 355 | 290 | 251 | 355 | 290
Qdiode [MJ] | 16 | 4 | 2.7 | 2 | 4 | 2.7
A. Verweij, EuroCirCol review 11-13 May 2016

## Slide 20: Layouts for the LBNL Block design
Nr of circuits per half-arc | 1 | 2 | 3 | 4 | 4 | 8
Nr of circuits entire FCC | 20 | 40 | 60 | 80 | 80 | 160
Magnets per circuit | 215 | 108 | 72 | 54 | 54 | 27
Inductance per circuit [H] | 26 | 13 | 8.6 | 6.5 | 6.5 | 3.2
Stored energy per circuit [GJ] | 8.6 | 4.3 | 2.9 | 2.1 | 2.1 | 1.1
Ramp time [min] | 20 | 20 | 20 | 20 | 20 | 20
VPC [V] | 555 | 277 | 185 | 139 | 139 | 69
VFPA,max [kV] | 1 | 1 | 1 | 1 | 0.5 | 0.5
VFPA,max,fault [kV] | 3.3 | 2.6 | 2.4 | 2.3 | 1.3 | 1.2
tcirc [s] | 333 | 166 | 111 | 83 | 166 | 83
Abusbar [mm2] | 880 | 622 | 508 | 440 | 622 | 440
Qdiode [MJ] | 8.6 | 4.3 | 2.9 | 2.1 | 4.3 | 2.1
A. Verweij, EuroCirCol review 11-13 May 2016

## Slide 21: Conclusion 1/2
Assuming tramp=20 min, VFPA,max=1 kV, tcirc≈200 s, gives:
Changing tramp (10-30 min) affects the rating of the converters (VPC and
PPC) but not the number of circuits.
 | Cos- | Block | Common coil | LBNL block
Nominal current [kA] | 10.275 | 8.47 | 9.03 | 25.8
Nr of circuits | 80 | 120 | 160 | 40
Magnet designers should try to minimize the stored energy. Cos- and block designs have clear advantages as compared to the common-coil design. But recent design of common coil with aux. coils is much better.
Subdivision of a 4 km long half-arc in several dipole circuits seems the most feasible solution for proper circuit protection within the required constraints, while at the same time having all converters and EE systems at the access points (using a SC link).
A. Verweij, EuroCirCol review 11-13 May 2016

## Slide 22: Conclusion 2/2
High voltage withstand levels of the circuits and all its components are needed to reduce the number of circuits and hence reduce the complexity of the layout.
I suggest to design several cos- and block dipoles with the usual EuroCirCol requirements, but with Inom=15-25 kA.
A. Verweij, EuroCirCol review 11-13 May 2016
High-current low-inductance magnets are favourable in terms of quench voltage and number of circuits, which seem to outweigh the drawbacks. Another advantage is shorter unit lengths, hence increasing the production yield of the conductor.

## Slide 23: Final remarks
Large tcirc in combination with large magnet stored energy will result in significant magnet-to-magnet quench propagation, hence very long cryogenic recovery. Thermal magnet-to-magnet propagation and possibilities to cryogenically decouple the magnets should be studied. This might have an impact on the spacing between dipoles (hence integrated field).
A. Verweij, EuroCirCol review 11-13 May 2016
The possibility of independent powering of the dipole apertures, each in series with a RQD/F circuit, should be explored from optics point-of-view. This might significantly reduce the number of busbars, power converters, DFB’s, and current leads.
The tunnel layout should foresee space for an additional cryo link to power the circuits.
Connection from the link to the circuits should be studied, as this might also affect the spacing between the dipoles.