| INFRASTRUCTURE PROJECT PROPOSAL SM18 Extension for Superconducting RF |  |  |  |  |
| --- | --- | --- | --- | --- |
| CONSOLIDATION |  |  | NEW INFRASTRUCTURE |  |
| STEP 1: Proposal FORMULATION |  |  |  |  |
| Originator: Frank Gerigk, Karl Schirm BE-RF Motivation: available space for assembly and testing of superconducting RF modules does not match the HL-LHC requirements. Brief description and scope: The proposal is to extend building 2173 (SM18) laterally on the North-West side to create 600 m2 of additional space for activities related to the preparation of superconducting RF modules (e.g. crab-cavities, LHC spare cavities, LHC/HL-LHC lower or higher harmonic cavities, etc.): storage for assembly parts, assembly area for modules that can further be tested in the existing nearby test-benches, as well as extension of the high power testing environment, including space required to provide adequate shielding. |  |  |  |  |
| Indicate what space will be freed by the realisation of this project: No space will be freed. Justify the allocation of the freed space: NA |  |  |  |  |
| MAIN Technical PARAMETER |  | MAIN PROJECT PARAMETER |  |  |
| Infrastructure Type (M/T): |  | Consolidation scope items included: |  | None (TBC) |
| Surface (m2) | 600 | Schedule estimation: |  | Before 2017 |
| Crane: | 10t | Non consolidation funding contribution: |  | All |
| Process Heating and Cooling: |  | MasterPlan evaluation |  |  |
| Electrical Power: |  | Budget estimation: |  | 3MCHF |

| STEP 2: GTPE VERIFICATION | STEP 3: Site Committee DECISION | STEP 4: Preliminary study |
| --- | --- | --- |
| Rejected. Verified with Rs = | Rejected. Accepted for preliminary study |  |
| Date of VERIFICATION: | Date of APPROVAL: | Date of STUDY: |
| Decisions of the Enlarged Directorate |  |  |
| STEP 5: PROJECT DECISION |  |  |
| Rejected. Accepted for execution. |  |  |
| DATE OF APPROVAL: |  |  |
| Actions to be undertaken: |  |  |
| Schedule of Implementation:. |  |  |

| # reasons for change | by the originator |
| --- | --- |

## Motivation

In recent years the infrastructure for constructing, treating, and testing of superconducting RF cavities has been upgraded substantially using the SRF R&D budget of the BE-RF group and project money. This includes items such as: a contribution to a new Electron-Beam Welding machine (EB) capable of welding Nb cavities (Bldg 112), a new Electro-Polishing installation (Bldg 118), upgrade and extension of the existing clean room in SM18, construction of a new clean room for HIE-ISOLDE cavities, a new High-Pressure UP-Water Rinsing facility connected to the first clean room, upgrade of the cryogenic distribution lines (partially funded by cryogenics) to enable testing at 2 K in the horizontal bunkers, upgrade/consolidation of  the vertical cryostats (incl. cryogenics) and their assembly stations, purchase of a 704 MHz klystron and associated waveguide equipment for a MW class RF test stand, optical inspection bench for cavities, establishment of a cavity reception area in building 252 with cavity tuning benches and low power RF measurement facilities, new coating stands for HIE-ISOLDE quarter wave and LHC 400 MHz cavities, etc.

This infrastructure has already enabled the assembly and testing of the Nb on Cu HIE-ISOLDE cavities into their first two cryo-modules and has led to the successful commissioning of these modules at HIE-ISOLDE. Furthermore, the SRF team has pushed the performance of 704 MHz 5-cell cavities from initially 3 MV/m at a Q=2x109 (first tests in 2014) to state of the art values of 22 MV/m at a Q>10x10 in 2016. At the same time LHC modules and first CRAB cavities for LHC have been RF processed and tested successfully. This progress clearly shows that CERN has re-established a functional SRF infrastructure that allows state-of-the-art production and R&D on superconducting cavities.

## Limitations

With the sophisticated technical infrastructure improving, also the demands for further SRF activities are rising and expose some serious limitations on simple infrastructure, namely: shielding, assembly and storage space. During the tests of the high-gradient 704 MHz cavities, the maximum gradient was limited by inadequate X-ray shielding in the test areas. The program aims at 25 MV/m in a cryo-module, meaning that values around 28 MV/m should be achieved during vertical cavity tests. Neither the vertical nor the horizontal bunkers can cope with the expected X-ray levels and additional shielding (concrete blocks) and access chicanes need to be put in place.

The testing of further CRAB cavities and the assembly of related cryo-modules is foreseen for 2017 but the present space for the RF systems between the two horizontal bunkers only allows the installations of the RF for CRAB or for the high-gradient module. Both RF systems are either existing or already funded by present programs but, without floor space, they cannot be installed in parallel with the existing LHC RF system, needed for the LHC modules. This will become worse if a 200 or 800 MHz RF is needed for the testing of lower or higher harmonic SRF modules for the LHC, or FCC study. The same problem occurs for the reception, storage, and assembly of cryo-modules for HIE-ISOLDE, CRAB, high-gradient, and future LHC modules. The present area in SM18 only offers assembly space for one of these programs, without providing even enough storage for a single SRF program. The originally foreseen space in SMA18 is now fully occupied by magnet activities. Without an adequate reception and assembly area for cryo-modules, it will not be possible to make efficient use of the already established SRF infrastructure mentioned above. This affects not only the already existing R&D programs but becomes worse when considering collaborations (e.g. with ESS and JLAB), which are meant to further increase CERN’s knowledge and capabilities of developing SRF cavities for future accelerators on the CERN site (e.g. FCC). It goes without saying that the cryo-module assembly areas have to be in close proximity to the clean processing and the high-power RF test bunkers to minimize contamination and transport risks.

| # PROPOSAL description | by the originator and/or GS-SE |
| --- | --- |

## BUILDING REQUIREMENTS

### Space requirements

Minimum of 600 m2.

### Handling REQUIREMENTS

Built in travelling crane with 10 t capacity.

Access for trucks for loading and unloading on either side.

### Building specification and external layout

Light building structure is adequate. The layout will take away some 15 parking spaces on the tarmac alongside SM18; the circulation is unaffected.

### Electrical power and HVAC REQUIREMENTS

#### Building requirements

HVAC requirements for SM18 should be extended to cover this extension. Whether the extension volume extends directly the SM18 volume or the two volumes are kept separated is still under study from the process point of view.

No major additional power request from the building itself.

#### PROCESSes requirements

Under evaluation: We do not expect major power requirement for the storage and assembly area.

## PROPOSED LOCATION

In order to profit from the already established SRF infrastructure in SM18 (and other places around CERN) we propose to extend the RF area in SM18 towards the parking lot as indicated in Figure 1. This would provide a floor space of approximately 7.5 m x 80 m = 600 m2 with the same height as the present SM18 building. This width still leaves a 7.5 m wide passage for trucks alongside the extension. This extension is meant to provide:

- A reception, assembly, and storage area for cryo-modules;

- Space to increase the X-ray shielding of the horizontal bunkers;

- Space for RF power generation in order to perform high-power RF testing of more than 2 structure types;

- Space for reception, assembly, and testing of high-power RF couplers.

The area shall be equipped with an overhead crane, rails, and shelves and does not need any sophisticated infrastructure. For a preliminary price estimate one can compare with the recently erected BAF3 building, which has around 750 m2 floor space plus a 550 m2 mezzanine and which is also equipped with an overhead crane. BAF3 was built for ~2 MCHF. Due to the different shape and different overhead crane configuration we estimate that the proposed extension of SM18 should be feasible within a 3 MCHF budget (pending a detailed study).

This extension is needed to efficiently use the already existing SRF infrastructure and should be regarded as a long-term solution to cover the needs of presently foreseen R&D and prototyping efforts. The extension plus the existing infrastructure will not be sufficient for larger series productions, which CERN typically makes in industry.

Planning and construction time should be within 2-3 years, possibly shorter (pending a detailed analysis). The building will be needed when the testing of CRAB cavities and the testing of the 704 MHz high-gradient module starts in spring 2017. Not solving the space problem until then will have a schedule impact on these programs.

An assembly, storage, RF area further away from SM18 is not considered useful because:

- this would involve risky transports from the assembly and storage areas to the clean rooms,

- it would not solve the floor space limitation to install more RF systems for high-power tests in the 2 existing bunkers.

So unless the complete SRF infrastructure is moved to a new place without delay, the proposed extension is regarded as the most economical solution.

## PROPOSED LAYOUT

### AVAILABLE SURFACES

The extension is proposed over the parking lot adjacent to SM18.

### INTERNAL DISTRIBUTION

On one side closer to the main entrance of SM18, alongside the area where the cleanroom is installed, there will be a small store for parts for cavity assembly and a cavity assembly area. The assembled cavities can then be carefully transported, similar to ROCLA magnet transport, to the adjacent clean room facility for further assembly and treatment. On the other side, closer to the power side, the extension will provide shielding for the cavity test-stands in SM18 allowing for tests at full gradient, and an area where powering equipment can be relocated, thereby freeing one bunker for an additional test stand to complete the SRF programme for LHC and HL-LHC.

### DESIGN LOADS

Same design loads as for SM18 hall itself. There is no underground structure to be particularly protected with possible exception of one cable trench from a nearby transformer to SM18.

### HANDLING FACILITIES

Handling of 8m long cryo-modules between the assembly area, object of this proposal, and the testing area, existing within the SM18 building. We plan that this does not require modifications to the pillars or structure of SM18. Note that the travelling crane of SM18 will not reach the extension. A crane is foreseen in the extension that will not reach SM18 itself. For cavity transport we plan on using robots like the ROCLA’s used in SM18 for transport of cryo-magnets (circa 15m and 15t) or dedicated trolleys. The question is open as whether we can use the existing ROCLA’s. We plan to make use of the porch at the entrance of SM18, built to protect the cryo-magnets during transport from SMA18 to SM18 for the same protection between the proposed SM18 extension and the SM18 building proper.

### ACCESS FACILITIES

The same access control that exists for SM18 can be extended to the proposed extension.

# PRELIMINARY DESIGN SUMMARY

## MASTERPLAN EVALUATION

In line with the masterplan.

## civil engineering

On 03 Dec 2015, at 08:41, Luz Anastasia Lopez-Hernandez <Luz.Lopez-Hernandez@cern.ch> wrote:

Bonjour Franck,

Je suis allée lundi sur le site avec Alick et Ghislain et j’ai regardé rapidement les conditions géotechniques de la zone.

A première vue, Je ne vois pas des problèmes particuliers en termes de génie civil. Il faudra recréer une série de portiques en charpente métallique fondés sur des semelles béton, un dallage comme l’existant et fermer le tout avec un bardage dument isolé.

Il faudra que vous décidiez de votre côté les ouvertures qui vous seront nécessaires entre le bâtiment existant et l’extension pour évaluer aussi leur faisabilité (éviter de toucher aux piliers, par exemple). Il faudra aussi que vous regardiez la distribution intérieure pour être sûr que les circulations intérieures sont ok, et que l’extension ne posera pas des problèmes pour la circulation de camions à l’extérieur (installations cryogéniques ? transfos ?).

En termes de services, il faudra rapprocher les groupes techniques concernés (EN-CV, EN-EL, etc.) car il me semble qu’il peut y avoir un travail important de dépose des centrales de ventilation existantes (en conflit avec l’extension) et de déroutage de services.

L’étude de l’ensemble devra suivre la procédure IPP pour que le projet d’infrastructure puisse être approuvé.

Pour le génie civil seul, je pense que tu peux partir, à cet stade, sur une enveloppe financière de 2,100 kCHF pour 600 m2 de surface au sol. A ceci il faudra ajouter le coût toutes les déposes préalables de services et l’installation des nouveaux services.

## TECHNICAL INSTALLATIONS

The usual technical installations can be foreseen. The high power electrical installations for cavity tests would remain in place and provide power to radio frequency amplifiers, which will be placed in the extension. The assembly and storage area require minimal amount of power.

The extension spans the space currently used by two ventilation units with large slanted hoods alongside the hall. A study will determine whether these units could be placed on the roof or at height or whether they would need to be kept within the extension, reducing the available area.

## OVERALL PROJECT SCHEDULE

The project should start in 2016 in order for the cavities to be installed in LHC during LS2 to be tested and available.

## Civil engineering schedule

There is no underground structural work to be done.

## Technical infrastructure schedule

| ## OVERALL cost, schedule & Resources The required budget is identified within the BE-RF group allocations. | by the originator, GS-SE and the other involved groups |
| --- | --- |

Estimated budget of 3 MCHF has been secured within BE-RF.

| ## impact on other items | by the originator and/or GS-SE and the other involved groups |
| --- | --- |

The building of the extension entails the suppression of about 15 parking spaces alongside SM18.

| ## comments (compulsory) | by GS-SE and HSE |
| --- | --- |

| ## comments (if required) | by other involved Group Leaders |
| --- | --- |

| # comments (If any) | by the Enlarged Directorate |
| --- | --- |