## Slide 1
MAIN STATUS | Symbol colour | PRIORITY
Not Connected | Grey | Highest Lowest
Invalid/undefined | Cyan | 
Device Alarm Unacknowledged | Red Blinking | 
Device Alarm Acknowledged | Red | 
Warning | Orange | 
Forced mode | Yellow | 
Device Under Range (HV instrument) | Dark Green | 
Device OK | Green | 
Data Quality and WARNING | Letter | Symbol colour | PRIORITY
Invalid data | N | Cyan | Highest Lowest
Old (connection with PLC lost) | O |  | 
Field object Error Warning | E | Orange | 
Warning (Feedback <> order or Manual/Force order <> Auto order) | W | No impact | 
Under Range (HV instrument) | U | Dark Green | 
MODE | Letter | Symbol colour | PRIORITY
Close Enable Mode | CE | No impact | Highest Lowest
Local Mode | L | No impact | 
Force Mode | F | Yellow | 
Manual Mode | M | No impact | 
Alarms and Interlocks | Letter | Symbol colour | PRIORITY
Hardware Pressure interlock | PR | Red | Highest Lowest
Full stop interlock (PLC software) | F | Red | 
Stop interlock (PLC software) | S | Red | 
Alarm (PLC software) | A | Red | 
Start interlock (PLC software) | I | No impact | 
Hardware Global interlock | G | Orange | 
Hardware Pressure open interlock | pr | Orange | 
Preventive close | pC | No impact | 
High threshold warning | H | Orange | 
Parameter high limit | L | No impact | 
Mask and Block info | Letter | Symbol colour | PRIORITY
Alarm Blocked (PLC) | B | No impact | Highest Lowest
Alarm Masked (only SCADA) | M | No impact | 
event Masked (only SCADA) | e | No impact | 
Comment is active
Lock: Device selected by another user (no action allowed)

## Slide 2
Current synoptic
VACUUM SYNOPTIC
UCPC-VAC Standard synoptic
UCPC-VAC Compact synoptic

## Slide 3
Vacuum Vessel Pressure
Ultra-High Vacuum
Rough Vacuum
-- Under Range --------------------------------------------------------------------------------------
-- 1 E-08 mbar <-------------------------------------------------------------------------------------
-- 1 E-06 mbar <-------------------------------------------------------------------------------------
High Limit
Limit value defines in Database can modified on the fly (SCADA)
Parameter Limit
Limit value defines in Database can modified on the fly (SCADA)
Hardware Limit given by the Gauge specifications
UR is Valid
(database attribute)
UR is not Valid
(database attribute)
Actions:
To be defined
No Action
Actions:
Laser Alarm
Send SMS Notification
No Action
(If required Alarm can be defined in Database)

## Slide 4
SPARE
WIDGET
ANIMATION