## Slide 1: LHCb UT & Velo CO2 transfer lines sizing – new flow values
30 October 2016
P. Tropea

## Slide 2: Operational parameters data from LHCb cooling meeting on October 13th, 2016 https://indico.cern.ch/event/568964/
 |  | UT 1/2 | Velo 1/2 | Main lines
Flow | g/s | 28.8 | 15.6 | 89
By-pass flow @ detector | g/s | 0 | 0.4 | 0.8
Flow used * calculations | g/s | 28.8 | 16 | 89.6
Power | W | 2500 | 1040 | 7080
Enthalpy heater power | W | 100 | 100 | 0
Power * calc | W | 2860 | 1254 | 9051
OD inlet | mm | 8 | 6 | 10
Thickness | mm | 1 | 1 | 1
ID inlet | mm | 6 | 4 | 8
OD return | mm | 18 | 12 | 26.7
Thickness | mm | 1.5 | 1 | 2.87
ID return | mm | 15 | 10 | 20.96
Length | m | 11 | 4.5 | 55
Volume |  |  |  | 
Volume liquid | l | 0.3 | 0.1 | 2.8
Volume gas | l | 1.4 | 0.2 | 14.7
Volume total | l | 1.7 | 0.3 | 17.4
Volume after JB | l | 3.1 |  | 
Total volume | l | 20.5 |  | 
Total flow in main lines = sum of both detector max needs (including local by-pass)
Flow always in by-pass at the detector level
includes 10% margin on each detector + 10% on total power
For each detector max flow & max power are considered
0.9 g/s for UT staves – 5 kW
0.6 g/s for each Velo module – 2 kW
2* Velo transfer lines volume + 1.5* UT transfer line volume (one branch is 2 times the length of the other)

## Slide 3: Main transfer lines @ -35 C max flow and power conditions
Return Dp ≈300 mbar
Max flow and power
Max power for UT only
Return Dp ≈180 mbar

## Slide 4: Heat pickup -35 C

## Slide 5: Main transfer lines @ +15 C
Return Dp ≈180 mbar
Max power for UT only
Return Dp ≈120 mbar
Max flow and power

## Slide 6: Summary of valves on the two plants & junction box
 | Valve P&I reference | Qty x1 system | Qty for 2 systems | Liquid or gas | Flow rate | Valve proposed | Cv | Dp @-40 | Dp @ 10
Transfer lines | PV1008, PV3010 | 2 | 4 | L | 100 | 8UW | 1.2 | 109 | 141
Junction box | PV3814 | 1 | 2 | L | 100 | 8UW | 1.2 | 109 | 141
Junction box | By pass PV3010 | 1 | 1 | L | 80 | 8UW | 1.2 | 69 | 90
Junction box | PV3A14, PV3C14 | 2 | 4 | L | 50 | 8UW | 1.2 | 27 | 35
Transfer lines | PV1008, PV3010 | 2 | 4 | L | 100 | HP9008 | 1.02 | 150 | 195
Junction box | PV3814 | 1 | 2 | L | 100 | HP9008 | 1.02 | 150 | 195
Junction box | By pass PV3010 | 1 | 1 | L | 80 | HP9008 | 1.02 | 96 | 125
Junction box | PV3A14, PV3C14 | 2 | 4 | L | 50 | HP9008 | 1.02 | 38 | 49
Plant | PV1H56, PV1G56, PV1052 | 3 | 6 | L | 150 | HP9012 | 1.9 | 97 | 126
Transfer lines | PV1040, PV3036 | 2 | 4 | G | 80 | HP9012 | 1.9 | 600 | 300
Junction box | By pass PV3036 | 1 | 1 | G | 80 | HP9012 | 1.9 | 600 | 300
 | baseline | 8UW | 11 |  |  |  |  |  | 
 | backup | HP9008 | 11 |  |  |  |  |  | 
 | decided | HP9012 | 11 | (tested @ -25 and +15 with 80 g/s and 7 kW load) |  |  |  |  | 
P&ID reference link

## Slide 7: Effects of Dp on return line on the detector evaporation T

## Slide 8: Summary of limits
The pressure drops on the return line are driving the minimum evaporating T that can be reached at the exit of the detector
The pressure drop on the return line from the detector to the accumulator are due to the transfer lines and to the valves along this path
Transfer line contribution is about (by calculation) 0.3 bar when in backup mode (full flow and full power – 90 g/s & 7 kW). When operating one detector only on that flow we reduce Dp to about 120 mbar
Valve contribution may go up 600 mbar in worst case, lowers to 300 mbar in single detector operation (*2 for two valves in series)
The total of 1.5 bar Dp on the return lines translates into 3 C delta T at low T. – Effect can be further mitigated by a choice of a bigger valve and maintained down to about 2 C.

## Slide 9: References

## Slide 10: Transfer lines lengths by O. Jamet – 25 May 2016
53060 mm from the alcove to the box
52800 mm from the alcove to the box
4180 mm from the box to the velo
4050 mm from the box to the velo
10800 mm from the box to UT
5000 mm from the box to UT