## Slide 2: SPECIAL CRG-TM: EYETS 2016 CRG coordination meeting
TE-CRG-ME
21 November 2016
S. Junker / J. Metselaar

## Slide 3: CRG-ME : LHC consolidations
LHCA Linde Desmi Oil Pumps LHC P4/6
  Installation of downstream “regulation valves”
ATLAS SR
  Installation of oil pump with magnetic coupling
ATLAS MR CP2
  Installation of volumetric oil-pump
LHCB-P18
  Installation of prototype oil pump with magnetic coupling
  QSCB-18-CP3 Change of oil injection connectors to allow oil injection regulation
LHCC P2 QSCCA-2-CP2
  Installation of missing damper
LHC-P4 QSCA-4-CPA
  Study of alignment issue
LHC-P6 QSCA-6-CP1
  Installation of prototype IMO oil pump skid

## Slide 4: CPs major overhauling
Running hours difference ~1600 hours between CP1 and CP2
 | EYETS 2016/2017 | Yets 2017/2018 | LS2
greater 40'000 | 0 | 1 | 9
Between 32'000 and 40'000 | 2 | 8 | 41
Between 24'000 and 32'000 | 9 | 42 | 21
Between 16'000 and 24'000 | 40 | 20 | 2
Between 08'000 and 16'000 | 23 | 4 | 2
Between 0 and 8'000 | 5 | 2 | 2
EYETS 2016/2017: No compressor to be sent for major overhauling
Total running hours difference ~11’000 hours between CP1 and CP4

## Slide 5: CRG-ME : issues for decision of actions
Concerns :
Vibration issues and improvement like balancing, alignment;
  Caused by a lack of analysis expertise and a lack of communication S176 has not yet given any recommendation for machine improvements.
Work orders type PM
  Decisions from the PM steering group meetings 2015 not yet fully implemented;
  Status change to «R-lance» not fully automatic;
  Status RADA-Accepte et Differe pour attente acces » created and used also for WO on compressor stations
Equipment Running hours counters;
  Not fully reliable for compressors, oil pumps;
  Not reliable also for the other equipment
Procedures and related documents
  Actually no procedure concerning mechanical tasks are approved;
  A lack of quality and QC is still noted for the LHC-TS tasks concerning preparation, performance and documentation

## Slide 6
CRG-ME : EYETS Work Orders (QCSM)

## Slide 7
CRG-ME : LHC Work Orders (QCSM) (1)

## Slide 8
CRG-ME : Work Orders (QCSM) (2)

## Slide 9
CRG-ME : Work Orders (QCSM) (3-consolidations & projects)

## Slide 10
CRG-ME : Work Orders (QCSM) (4)
(See planning MS-Project)
Also: BA6, BA7,…
HIE-Isolde

## Slide 11
Many thanks for your attention

## Slide 12: Pump curve Desmi oil pump

## Slide 13: LHCB boosters discharge temperatures
Chart: LHCB point
| 18 | 4 | 6 | 8
CP-1 | 77.5 | 79.4 | 86 | 84.4
CP-2 | 75.5 | 79.7 | 86.6 | 84.4
CP-3 | 73.4 | 76.5 | 78.7 | 84.4

## Slide 14: Lack of damper