## Slide 1: Structural characterization of silicon channels for fluidic applications
Richard Meunier
Diego Alvarez Feito, Clémentine Lipp, Alessandro Mapelli, Jerome Noel

## Slide 2: Introduction
Thermal management of detectors electronics
  Cooling large surface detectors
  Keeping the detectors cool at all time
Problems and constraints
  Confined space with very limited access
  Different types of liquid coolants
  Using material with low particle interaction
Envisioned solution
  Silicon micro-channels
  Ideally integrated in a monolithic detector

## Slide 3: NA62-GTK – SILICON MICROCHANNEL COOLING
NA62 is the first experiment to use silicon microcooling plates for the thermal management of their GTK pixel detectors (since 2014).
3 detector modules
Liquid C6F14
Top below -10ºC
Power dissipation 25W-48W over 6x4cm2
A. Mapelli et al. 2012 JINST 7 C01111
P. Petagna et al., Microelec. Journal 44 (2013) 612–618
G. Romagnoli et al., Microelec. Eng. 145 (2015) 133-137

## Slide 4: Silicon Microchannel Cooling
Why Silicon or SiC?
  Detectors are in silicon
  Controlled interaction with particles
  Availability
  Extensive processing knowledge and technologic applications (Micro-electronics, MEMS, etc)
Interest and goals:
  Size advantage
  Design advantage: large pattern possibility
  Can be integrated in the detector’s fabrication process combining versatility of standard micro-fabrication processes with high thermal efficiency of micro-fluidics
Mechanical problematics:
  Young’s modulus of 169 GPa <110> or 130 GPa <100> or 187 GPa <111> or…?
  Possible fatigue in monocrystalline silicon can accumulate and lead to rupture
  Lots of publications and tests on silicon mechanical properties, but so far no link between them…

## Slide 5: Micro-Channel Fabrication
Two different approaches:
  Wafer bonding
  Buried micro-channels
Wafer bonding
  Etching step
  Wafer bonding
  Problem: wafer bonding can be tricky
WAFER BONDING APPROACH

## Slide 6: FBK-CERN Embedded Channels
Buried channels
  Trench through Bosch Process etching
  Channel engraving with SF6 isotropic etching
  Channel filling with PE/LPCVD poly-silicon

## Slide 7: Characterization
Objective at CERN: defining a standard procedure to validate and ensure reliability of the cooling systems  Leak test and pressure tests
Reasons to perform pressure tests:
  Gaining a better understanding of the mechanical response of ScSi
  Assess effect of channel geometry to optimize design of new devices
  Evaluate wafer-to-wafer bond strength
  Serve as quality control procedure
LHCb VELO
ALICE ITS
NA62 GTk

## Slide 8: Leak Test
Pumping and leak recording
Objective:
Testing if samples are leak tight
Positioning

## Slide 9: Pressure Test: Setup
Air
Manual Pump
Connector
Sample
H2O
Pressure sensor
DAQ + Control
Water

## Slide 10: Safety Chamber

## Slide 11: Sample Holder

## Slide 12: Sample Positioning

## Slide 13: Pressure Test & Acquisition

## Slide 14: Failure

## Slide 15: Results
Si-Si wafer bonding:
  Good implementation
  Pressure resistance depends on boding quality and channel geometry
Single-channel samples
  Etched together with real cooling devices for quality control of bond strength

## Slide 16: Observed with Si-Si bonded channels
Example of Si-Si bonded channel failure:
Break visible to the naked eye
Repeatable pressure at rupture
Si-Si bonded sample design
P06_B12: Graph of pressure vs time, sharp decrease of pressure at failure

## Slide 17: Failure in Silicon Cover

## Slide 18: Experimental Results: Typical Failure Models
Interfacial Failure
  Clean surfaces observed after testing suggest poor wafer bonding

## Slide 19: Experimental Results: Typical Failure Models
Silicon Failure
  Good bonding often results in the explosion of the channel cover

## Slide 20: Results
Buried micro-channels:
  Challenging process
  Very good leakage and pressure resistance
Two types of channels:
  Longitudinal channels
  Transversal channels
Pressure test @250-300 bars

## Slide 21: Pressure Samples Longitudinal
trench
Buried channel
inlet
P1 = 25
W = 50; 100; 200; 350
P1
W
P1
W/#
of channels
SINGLE: P_S_L_CX_W50
RAMIFIED: P_R_L_CX_W50
W
W/# of channels

## Slide 22: Failure in a Longitudinal Sample @ 236 bar

## Slide 23: Pressure Samples Transversal
W
P1 = 25
W = 50; 100; 200; 350
SINGLE: P_S_T_CX_W50
P1
RAMIFIED: P_R_T_CX_W50
P1
W/# of channels

## Slide 24: Failure in a Transversal Sample @ 300 bar
Transversal/Single/W=50, exploded at 335 bar

## Slide 25: Monolithic Integration
If not CMOS compatible  separate channel processing, with direct wafer bonding at the end
If CMOS compatible  direct integration at the end of detector processing
Ultimate objective: monolithic bloc for the detector requiring minimum intervention once installed

## Slide 26: Full integration

## Slide 27: Conclusion & Outlook
Thermal management represents a major challenge in HEP.
Continuous advances in micro-engineering have opened the door to the development of smaller and more efficient cooling devices capable of handling increasing power densities with a minimum mass penalty.
AIDA-2020 is bringing together a community to develop and study silicon microchannel cooling devices and low mass mechanical structures .
By 2019, a catalog of building blocks, design guidelines and standards for characterization and qualification of devices and systems for microchannel cooling (single phase and evaporative) will be available.
Long term objective:
    Fully understanding failure parameters and how to avoid failure
  Full-proof characterization and reliability protocol
SCOPE OF AIDA-2020 to gather this knowledge and bring building blocks together

## Slide 28: The End
Thank you for your attention!