## Slide 1: New CERN CO2 Test Facility for Mini- and Micro-channels WP 9 - D9.1 AIDA Annual Meeting Paris Desiree Hellenschmidt, Paolo Petagna EP-DT-FS CERN, Geneva, Switzerland

## Slide 2: OVERVIEW
Motivation
Approach
Test facility
Research plan
Conclusion

## Slide 3
MOTIVATION
REQUIRED:
Internal standard to test
μ-channel cooling devices

## Slide 4
MOTIVATION

## Slide 5
MOTIVATION
MAIN OBJECTIVE:
Characterization of
thermal properties and
pressure drop behavior of
μ-channel cooling devices

## Slide 6
Definition of common needs for the institutes
Resources available at CERN
Definition of the state-of-the-art test stand
active re-definition of a
high quality test stand
APPROACH
BALANCE
BALANCE
BALANCE

## Slide 7
Common parameters of interest
mass flux
fluid pressure
fluid temperature
heat dissipation
pressure drop
Resources available at CERN
evaporative CO2 is the chosen refrigerant
Transportable Refrigeration Apparatus for CO2 Investigation = TRACI developed at CERN
  CO2 is an eco-friendly alternative
  mass flux is adjustable (by-passing)
  temperature range from ~ +20 to -25 ̊C
  CO2 is re-circulated
APPROACH
Fig. 1 CO2 refrigeration apparatus at CERN

## Slide 8
State-of-the-art test stand extended version
APPROACH
Parameters under test | Method
Fluid flow properties | DIRECT: Flow visualization with high speed camera
 | INDIRECT: Temperature & pressure sensors
Heat transfer | DIRECT: Temperature measurements in the flow and on surrounding equipment
 | INDIRECT: Heat transfer visualization with infrared camera
Pressure drop | Absolute & relative pressure transducers

## Slide 9
APPROACH
2-phase CO2
Transportable Refrigeration Apparatus for CO2 Investigation
Vacuum vessel
Adiabatic test conditions for more accurate heat transfer measurements
P & T sensors
High precision measurements for pressure & heat transfer
Flow meter
Direct high precision measurement of the mass flow rate
High speed cam
IR Camera
Heat transfer visualization
Visualization of details on bubble dynamics
(100 000 fps)
+ Data acquisition
More controlled measurement surroundings are ensured by following components:

## Slide 10
TEST FACILITY
CO2
temperature
sensors
pressure and temperature sensors before and after the experiment
( Measurement points = MP1 to MP4 )
temperature sensors on the experiment
two Peltier elements
as pre- and
post-heater
Mock-up heater (Joule Heater)
Fig. 2 Schematic of the new CO2 test facility

## Slide 11
TEST FACILITY
Fig. 3 Design of the new CO2 test facility
pressure and temperature sensors before and after the experiment
( Measurement points = MP1 to MP4 )
temperature sensors on the experiment
two Peltier elements
as pre- and
post-heater
Mock-up heater (Joule Heater)
MP1
MP2
MP3
MP4

## Slide 12
TEST FACILITY
Fig. 4 Schematic of the new CO2 test facility with vacuum vessel
Fig. 5 Experiment section and vacuum vessel of the new CO2 test facility

## Slide 13
TEST FACILITY
INFRA-RED CAMERA
HIGH SPEED
CAMERA
EXPERIMENT
Fig. 6 Vacuum vessel of the new CO2 test facility

## Slide 14
TEST FACILITY
Fig. 8 New test facility for evaporative CO2 flow measurements in mini- and micro-channels (II)
Fig. 7 New test facility for evaporative CO2 flow measurements in mini- and micro-channels (I)

## Slide 15
TEST FACILITY
Fig. 10 Experiment section within the vessel
Fig. 9 Differential & absolute pressure sensors and flow meter outside the vacuum vessel

## Slide 16
TEST FACILITY
DATA AQUISITION with LabVIEW®
experiment sensors
flow meter
vacuum level
temperature inside vacuum vessel
control of Peltier & Joule heater
online-evaluation of fluid state
acquisition in parallel with cameras possible
→ MATLAB® code for analysis

## Slide 17
Chart: temperature test @ room temperature
TEST FACILITY
SENSOR CHECK: Temperature
Δ = 0.3 ̊C

## Slide 18
TEST FACILITY
SENSOR CHECK: Pressure
Chart: pressure test abs @ atmospheric pressure
Δ = 0.3 bar
Chart: pressure test diff @ atmospheric pressure
Δ = 0.005 bar

## Slide 19
RESEARCH PLAN
GOALS for experimental research on evaporative flow of CO2 in mini- and micro-channels at CERN:
Create a larger and reliable database for CO2 pressure drops, heat transfer coefficient and flow patterns in mini- and micro-channels for model upgrades
Extend research towards negative fluid temperatures and micrometer sized channel diameters
Find and test a theoretical micro-channel definition

## Slide 20
RESEARCH PLAN
STEP 1 : Test simple single channels / tubes (ID < 2 mm)
To address the complexity of the physical processes occurring in micro-channels and for their better understanding
STEP 2 : Test more complex channel geometries
To address the immediate need for micro-channel cooling in HEP experiments using the gathered insights and results from Step 1

## Slide 21
RESEARCH PLAN
STEP 1:
ROUND SINGLE CHANNELS
SQUARED SINGLE CHANNELS
Stainless Steel |  |  | Glass (Borosilicate) |  |  | Titanium | 
ID [mm] | OD [mm] |  | ID [mm] | OD [mm] |  | ID [mm] | OD [mm]
0.13 | 1.58 |  | 0.1 | 0.17 |  | 0.3 | 1.58
0.25 | 1.58 |  | 0.15 | 0.25 |  | 0.5 | 1.58
0.5 | 1.58 |  | 0.2 | 0.33 |  | 0.8 | 1.58
0.75 | 1.58 |  | 0.3 | 0.4 |  |  | 
1 | 1.58 |  | 0.5 | 0.7 |  |  | 
1.5 | 3.175 |  | 0.7 | 0.87 |  |  | 
2 | 3.175 |  | 0.8 | 1 |  |  | 
 |  |  | 1 | 1.2 |  |  | 
 |  |  | 1.5 | 1.8 |  |  | 
 |  |  | 2 | 2.4 |  |  | 
Glass (Borosilicate) |  |  |  | 
inner cross-section [mm] |  |  | wall thickness [mm] | 
0.1 x 0.1 |  |  | 0.05 | 
0.8 x 0.8 |  |  | 0.16 | 
0.3 x 0.3 |  |  | 0.15 | 
0.2 x 0.2 |  |  | 0.1 | 
1.0 x 1.0 |  |  | 0.2 | 
0.5 x 0.5 |  |  | 0.1 | 
0.7 x 0.7 |  |  | 0.14 | 

## Slide 22
RESEARCH PLAN
Micro-channel definition
based on the preliminary work of Y. Moussy
a possible definition was found
by means of the bubble departure diameter
RESEARCH PROPOSALS for STEP 1:
VALIDATION
PENDING
?
VALIDATION
PENDING

## Slide 23
Internal setup to test μ-channel cooling devices is completed
Uncertainty level of the experiments can be limited
Test stand allows for a wide temperature range
CO2 is an eco-friendly alternative to other refrigerants
Component test finished
Research program launched for first tests
CONCLUSION

## Slide 24
Control the new setup for flow of evaporative CO2 in μ-channels
Carry out measurements
Compare results with literature
Use findings for better understanding of the physical behaviour of the flow in μ-channels
OUTLOOK

## Slide 25
...
…g blue
Notes: Invitation for all AIDA members to come to Cern and do their testing!