## Slide 1: Update on Junction Box Design
Edyta Pilorz
(Cracow University of Technology)

## Slide 2: Pipe work
Construction drawings:
Prepared
Checked
Production in progress

## Slide 3: Pipe work – quality verification
Quality verification; steps:
Visual inspection in the DT workshop (66 welds from 210 checked already)
Visual inspection in EN-MME
10% of welds to be checked with X-rays

## Slide 4: Clamping plastic parts
Construction drawings:
24 drawings prepared
Checking in progress
To be sent to the production after the check (material: polyethylene)

## Slide 5: Construction of the box
Construction of the box:
3D model to be finished
Construction drawings to be done

## Slide 6: Order status
We are waiting for the delivery of:
Carel valves
Watlow heaters
Material for the box (insulation panels and aluminium profiles)
Some fittings

## Slide 7
Main Patch Panel Location
To detector C side
To JB and detector A side
Electrical patch panel location

## Slide 8
Wago 2002-1201
Wago 2002-3203
Width | 10.4 mm
End cover width | 1 mm
Length | 46.2 mm
Height NS 35/7,5 | 39.9 mm
Height NS 35/15 | 47.4 mm
Height NS 32 | 44.9 mm
Phoenix MTKD-NICR/NI - 3100062
800x400x150 mm
Door open
0.93x60 cm
10 cm
10 cm
4.9 cm
4.9 cm
800x600x200 mm
0.93x60 cm
10 cm
4.9 cm
4.9 cm
NSYS3DB4815
GSM cable
Gas pipes
~25cm
~25cm
NSYS3D8620
Inputs
Inputs
Outputs
Outputs
600
800
200
60cm
90 ˚ turn
Electrical patch panel

## Slide 9: Fitting the “Junction Box” in the alcove - test
Scale: 1:1
This helped us to see how to route the cabling
It is visible where to fix the support for the box

## Slide 10: Placing the cooling plants in UX85 alcove - layout
1st cooling plant
2nd cooling plant
1st accumulator
2nd accumulator
1st chiller
2nd chiller
3 electrical cabinets

## Slide 11: Measurements for the passage from the lift up to the alcove
LIFT
Width: 793 mm
Length: 1964 mm
Height: 2395 mm
W
H
L
ENTRANCE AFTER THE LIFT
Height: 2400 mm
H
PASSAGE
Height: 2090 mm
H

## Slide 12: Dimensions of the shaft hole (lifting platform)
1436 mm
964 mm
WALL
STAIRS
.
740 mm

## Slide 13: The biggest dimensions which we can transport vertically
793 mm – because of the width of the lift’s door – TO BE CHECKED WITH NEW LIFT
1436 mm – because of the size of the hole in the lifting platform in the alcove which is 964 mm x 1436mm
2080 mm – because of the height of the passage