## Slide 1: Bulk power for CMS 20170913
M. Hansen, CERN
S. Lusin, CMS TC / UW

## Slide 2: Bulk power system
Exploit the fact that we know our environment
  Compare to initial construction
  Allow smaller safety factors

## Slide 3: Bulk power system
Tracker
  Will make use of DCDC converters in or close to the front end
  Remote bulk supply
  “Fine grain” power distribution, safety and monitoring
  System will need some space in USC55 for controls
Barrel Calorimeters
  Similar to Tracker
Endcap calorimeter
  Under study; potentially different to barrel as supplied through cable chain or due to internal space limitations

## Slide 4: Tracker
100kW
This implementation
  may, depending on the location of the active components, require radiation and / or magnet field qualified equipment
12V
Power bank
Patch panel
Distribution
Monitoring
Patch panel
by detector
Patch panel
by detector
Patch panel
by detector
Patch panel
on detector
Patch panel
on detector
Patch panel
on detector
Detector
POL
Detector
POL
Detector
POL
20-80m
6m
2m

## Slide 5: Barrel Calorimeter
12V
Power bank
Patch panel
In tower
Distribution
Monitoring
Patch panel
on detector
Patch panel
on detector
Patch panel
on detector
Detector
POL
Detector
POL
Detector
POL
20m
15m
3m
200kW
This implementation
  implies radiation and magnetic field tolerance qualification of the active equipment

## Slide 6: Endcap Calorimeter alt. 1
12V
Power bank
Detector
DCDC
Detector
DCDC
Detector
DCDC
Local
Regulator
Local
Regulator
Local
Regulator
20m
2m
Patch panel
Distribution
Monitoring
20m (fixed, disconnectable)
100kW + 100kW
This implementation
  Allows operation only in a discrete number of positions, e.g. fully closed and fully opened

## Slide 7: Endcap Calorimeter alt 2.
12V
Power bank
Detector
DCDC
Detector
POL
Detector
POL
Local
Regulator
Local
Regulator
Local
Regulator
20m
2m
20m (fixed, disconnectable)
Patch panel
Distribution
Monitoring
Line
Protection
35m (chain)
100kW + 100kW
This implementation
  Allows full operation in a discrete number of positions, e.g. fully closed and fully opened and partial operation, e.g. monitoring, in any position

## Slide 8: Requirements
Requirements
  About 12V; not much higher at any time
  Modular
  High availability: configured for n+1 or n+2 redundancy
Wishes
  Light and compact
    To make carrying around less demanding
  Affordable
    Low cost would not hurt unless quality suffers
    Generally means high volume COTS

## Slide 9: Requirements
In addition…
  Sufficiently magnetic field tolerant
    200 Gauss < Fringe field in CMS cavern < 1100 Gauss
      200 Gauss in X0 and balconies, 1200 in towers around the crack between YB and YE
    Qualification procedure required
  Sufficiently radiation tolerant

## Slide 10: UXC55
X0
X4
X3
X2
X1

## Slide 11: Radiation levels
Low total dose in X0
  Estimation after 3000 fb-1:
    Hadrons > 20 MeV = 2.1*108/cm2
    1 MeV-equivalent neutrons = 6.7*109/cm2
  Source: CMS BRIL
Will have to deal with SEE
  SEU, SEB
  i.e. how do the PS fail following SE?
What about X3/X4?
  Will be determined after further simulation by CMS BRIL

## Slide 12
CMS magnet fringe field in UXC55 with 3.8T at IP
Scale in mT, from 0 to 120 mT, with 5 mT increment
Horizontal mid-plane Y=0
Prepared by B. CURE with data from V. KLYUKHIN
November 2010
10
15
20
25
30
35
40 45
60
55
50

## Slide 13: Measurement of the fringe magnetic field (@3.8T)
X3F34
X3F35
X3F31
X3 BALCONY FAR
25-31 mT
18 mT
90%
X2F37
X2 BALCONY FAR
X2F36
25-27 mT
25-27 mT
90%
-Z
-Z
X0R11
X0U11
45 mT
25 mT
90%
-Z
X0 UPPER LEVEL
X0E11
35 mT
23 mT
90%
-Z
X0 UPPER LEVEL
X0 LOWER LEVEL:
21-27 mT
Nicola Bacchetta, Wolfram Zeuner May 19th 2016

## Slide 14: COTS Candidate / test engine
PowerOne PFE3000-12-069RA
12v 3kW (244A), 94% efficient
http://www.digikey.com/product-detail/en/bel-power-solutions/PFE3000-12-069RA/179-2714-ND/4439947
  31 in stock 20160429
  937USD for one, 8000 USD for 10 pc
  Estimated product life beyond 10 years

## Slide 15: PFE3000-12
S. Lusin

## Slide 16: PFE3000-12
S. Lusin

## Slide 17: Magnetic field test
S. Lusin

## Slide 18: Magnetic field test
S. Lusin, B. Cure

## Slide 19: Magnetic field test
Bottom line
  Tolerates 400g from side
  Tolerates 600g from top
  Tolerates 250g longitudinal
    A different test in the M1 magnet at CERN
S. Lusin, B. Cure

## Slide 20: Front end power distribution
Finer granularity than a single bulk supply
  Line protection
  Over/Under voltage protection
  Voltage monitoring
  Current monitoring
  (Power monitoring)
Example COTS
  LM25066: System Power Management and Protection with monitoring through PMB (essentially I2C)
Backend could be an ELMB+ system

## Slide 21: Front end power distribution
Final development, production and maintenance by Industrial partners
  Tuned to requirements for different users, e.g.
    Trip current depending on cabling to detector
    Combine LV and bias distribution for silicon trackers

## Slide 22: Plans
Demonstrate feasibility and reliability
  Performed 3D magnetic field tolerance mapping in M1 magnet
  Install demonstrator in UXC55 X0 lower floor for long term (B field) verification
Mixed field radiation studies
  @ Charm (CERN)
  Need to determine how an SEE affects an n+1 or n+2 redundant power supply system

## Slide 23: Plans
Collaboration with industry for development of power distribution and monitoring system
  Positive feedback from industrial partners, e.g. CAEN
  Tuned to each subsystem