## Slide 1: Cooling and Ventilation for HL-LHC (WP17.3) INTRODUCTION
Michele Battistin, Frederic Borralho, Alexandre Broche, Alejandro Mejica, Paul Pepinster
CERN
Engineering Department
Cooling and Ventilation Group
Cooling and Ventilation Technical Review – 14th March 2017

## Slide 2: Content
  Scope of the HL-LHC CV Review
  New HL Infrastructure
  Cooling Requirements
  General Planning of the Project
  Main Design Assumptions & Criteria
  Introduction to Cool & Vent Presentations

## Slide 3: Content
  Scope of the HL-LHC CV Review
  New HL Infrastructure
  Cooling Requirements
  General Planning of the Project
  Main Design Assumptions & Criteria
  Introduction to Cool & Vent Presentations

## Slide 4: Scope of the HL-LHC CV Technical Review
Examine the design of the cooling and ventilation systems;
Assess the proposed technical choices with respect to the needs including the system availability;
Assess the advancement status of the system “integration” (incorporation of CV equipment in the 3D model of the buildings);
Assess the preliminary installation schedule;
Comment the credibility of the plan, and the adequacy of available resources for the project.
What is the review “perimeter”?

## Slide 5: Scope of WP 17.3 – Cooling and Ventilation
  Cooling systems in point 1 and 5
  Ventilation systems in point 1 and 5
  General services (compressed air, fire-fighting water, demineralised make-up water, drinking water,…) in point 1&5
  Cryogenic equipment cooling in point 4
  Crab cavities bench test in SPS
Object of the review
Not object of the review
Who prepared and presents this review?
Notes: The second part is “less demanding”

## Slide 6: CERN - EN/CV Engineering Department Cooling and Ventilation Group
M. Battistin
P. Pepinster
A. Broche
F. Borralho
A. Mejica
Installation Maintenance and Operation
Operation Section
S. Deleval
Design Office and Works Supervision
DOW Section
Y. Body
Maintenance Procedures, Installation Inventory and CMMS
MA Section
G. Peon
Cooling Systems for Experiments Particle Detectors
DC Section
O. Crespo
Project Management and CFD studies
PJ
Section
M. Battistin
Control Systems
HW & SW
CL
Section
R. Barillère
CV Group
M. Nonis

## Slide 7: Content
  Scope of the HL-LHC CV Review
  New HL Infrastructure
  Cooling Requirements
  General Planning of the Project
  Main Design Assumptions & Criteria
  Introduction to Cool & Vent Presentations

## Slide 8
The Large Hadron Collider (LHC)
Point 1
ATLAS
Switzerland
Point 5
CMS
France
Globe & Reception
CERN Hostel
You are here
Notes: 8

## Slide 9: HL-LHC Underground Works

## Slide 10: HL-LHC Works at Point 1 (ATLAS)
Reception building

## Slide 11: HL-LHC Surface Buildings at Point 1
What these buildings will be used for?

## Slide 12: HL-LHC Surface Buildings at Point 1
Electrical Building
Head Shaft Building
Ventilation Building
Chilled Water Production
Cooling Towers
And Pumping Station
Cryogenic Compressor Building
Helium Tanks

## Slide 13: Underground Structures at Point 1
ATLAS
300 m
70 m
60 m
Let’s see Point 5 now:

## Slide 14: HL-LHC Works at Point 5 (CMS)

## Slide 15: HL-LHC Surface Buildings at Point 5

## Slide 16: HL-LHC Surface Buildings at Point 5
Electrical Building
Ventilation Building
Chilled Water Production
Head Shaft Building
Cooling Towers
Primary Water Circuit
Cryogenic Compressors Building
Helium tanks

## Slide 17: Underground Structures at Point 5
CMS
300 m
70 m
60 m
We review the cooling requirements now…

## Slide 18: Content
  Scope of the HL-LHC CV Review
  New HL Infrastructure
  Cooling Requirements
  General Planning of the Project
  Main Design Assumptions & Criteria
  Introduction to Cool & Vent Presentations

## Slide 19: Heat Load from Main Equipment
Equipment | Heat Power [kW] | Water | Air
Cryogenic compressors | 5000 | 96% | 4%
Radio Frequency equipment | 712 | 93% | 7%
DC power cables | 450 | 93% | 7%
Power converters | 317 | 86% | 14%
Cryogenic cold boxes | 300 | 78% | 22%
HV power supply | 256 | 72% | 28%
Machine protection system | 79 | 99% | 1%
Electronic racks | 68 |  | 100%
AC cables, transformers, etc. | 63 |  | 100%
Faraday cages | 15 |  | 100%
General services | 200 |  | 100%
Primary ventilation + pressurisation | 330 | 100% | 
Total | 7790 |  | 
The project will be done in two phases:

## Slide 20: From ½ Crab Cavities to Full Crab Cavities
Equipment | ½ CC [kW] | Full CC [kW]
Cryogenic compressors | 5000 | 5000
Radio Frequency equipment | 712 | (1424)
DC power cables | 450 | 450
Power converters | 317 | 317
Cryogenic cold boxes | 300 | 300
HV power supply | 256 | (512)
Machine protection system | 79 | 79
Electronic racks | 68 | 68
AC cables, transformers, etc. | 63 | 63
Faraday cages | 15 | (30)
General services | 200 | 200
Primary ventil + pressurisation | 330 | 330
Total | 7790 | (8773)
How will we manage this staging?

## Slide 21: 1/2 CC to Full CC Upgrade Strategy
Cooling pipes, ventilation ducts and main components sized for full CC
Equipment (pumps, AHUs, etc.) sized for ½ CC
Upgrade from ½ to full Crab Cavities configuration is possible with:
No new excavation works
No CV ventilation ducts and cooling pipes replacement
No EL main cabling replacement
When we will be asked to install our equipment?

## Slide 22: Content
  Scope of the HL-LHC CV Review
  New HL Infrastructure
  Cooling Requirements
  General Planning of the Project
  Main Design Assumptions & Criteria
  Introduction to Cool & Vent Presentations

## Slide 23: Civil Engineering Outline Schedule
Courtesy of Pieter Mattelaer
2017
Tender design
Construction tender
2018
Site mobilisation
Shaft excavation
2019-2020 (LS2)
Underground
Excavation Works
Start Concreting
2021
Underground
Finish Concreting
(2020-) 2021-2022
Surface Works
When technical infrastructure will be installed?

## Slide 24: Technical Infrastructure Schedule (Without Civil Engineering)
Time window for CV installation in surface buildings and underground areas
Connection of the HL-LHC buildings with LHC tunnel (UPR): ventilation of the safety SAS un UA
How CV is organising to get this result?

## Slide 25: Cooling and Ventilation General Schedule
Tendering process @ CERN
  8-12 months for Market Survey phase
  8-12 months for Invitation to Tender phase (for each contract - 5)
  Finance Committee for contract authorisation
  Contractor preparatory phase
    12 months for construction design and purchase phase
  Installation phase details at the end of the day…

## Slide 26: Content
  Scope of the HL-LHC CV Review
  New HL Infrastructure
  Cooling Requirements
  General Planning of the Project
  Main Design Assumptions & Criteria
  Introduction to Cool & Vent Presentations

## Slide 27: Project Guidelines
Main Design Assumptions
HL equipment separated from LHC and Experiments ones; HL tech. infrastructure installation during LHC run phase;
Interconnection of HL new systems with existing LHC installation when reasonable (redundancy, operation…)
Solution Pt1 = Pt5 (except heating network).
Main Design Criteria
Energy savings:
  Energy savings required by law;
  Energy recovery if economically justified (ROI < 10 years);
  Enlarged acceptable temperatures ranges in buildings (S&U);
  Redundancy on safety systems and critical systems;
  Access to underground areas during machine run.

## Slide 28: Content
  Scope of the HL-LHC CV Review
  New HL Infrastructure
  Cooling Requirements
  General Planning of the Project
  Main Design Assumptions & Criteria
  Introduction to Cool & Vent Presentations
Naming convention at first

## Slide 29: CV Circuits Naming Conventions @ CERN
Equipment with
conductivity requirements
Thermal load
with no special conductivity
requirement
Primary Water Circuit
Secondary Water Circuits
Demineralised
-water
Raw-water
Demineralised make-up water
Tap make-up water

## Slide 30: CV Circuits Naming Conventions @ CERN
Ventilation
Humidity Control
Ventilation
Air Cooling
Chilled water
5/6 ➡ 10/12 °C
Mixed water
14 ➡ 20 °C
Primary water
circuit
Chiller condenser
Water circuit
25°C

## Slide 31: HL-LHC Underground Building Names (Pt1)
ATLAS
UA13
UPR13
UL13
UR15
US17
UW17
UL17
PM17
UA17
UPR17

## Slide 32: HL-LHC Surface Building Names (Pt1)
SF17
SHM17
SD17
SU17
SE17
We enter now in the technical details of the CV design

## Slide 33
Ventilation
Paul Pepinster

## Slide 34
Cooling
Alexandre Broche

## Slide 35
Integration
Frederic Borralho

## Slide 36: …any question?
Thanks to:
Y. Body, F. Borralho, A. Broche, A. Mejica, P. Pepinster.

## Slide 37: BACK-UP SLIDES
Thanks to:
Y. Body, F. Borralho, A. Broche, A. Mejica, P. Pepinster.

## Slide 38: LHC Building Naming Convention
5
7
3
SU17
Location
S= Surface
U = Underground
P = Shaft (pit)
Use
F = Fluid
U = Ventilation
W = Water
H = Helium (Cryo)
E = Electricity
S = Service
L = Link
A = Power Supply
…
LHC reference
1 = Point 1 (ATLAS)
5 = Point 5 (CMS)
Position number
5 = interaction point
Growing clockwise

## Slide 39: LHC Buildings Naming List
Building name | Description
SF | Cooling towers + primary water circuit pumping station
SE | Electrical distribution
SHM | Cryogenic compressor building
SD | Head of the shaft
SU | Chillers for chilled and mixed water production + Ventilation
PM | Shaft for the material passage
US | Service cavern
UW | Cavern dedicated to secondary water circuits and U ventilation
UR | Connection tunnel
UA | Radio frequency and power supply
UL | Cryogenic and power supply services passage
… | …