Future Archiver (librarian)
for WinCC OA Control Systems
Piotr Golonka, Jakub Guzik, Rafal Kulaga
CERN BE-ICS-SDS
In Openlab collaboration with ETM/Siemens

---
Content
- WinCC OA archiver status quo
  - Deployments
  - Scale (example of BE/ICS applications)
  - Challenges
- NextGen archiver
  - Motivation
  - Architecture and technologies
  - Status

---
Archiver in a control system
- Essential element of SCADA (Supervision) layer
  - Stores the history of values and alarms
    (into a “database”)
  - Allows the operator to see the
    evolution of the process
    (historical trends)
  - Diagnostics and postmortem
    analysis “Event Screen”
- Entry point for Data Analytics
  - For industrial processes
  - … but also for physics analyses (“conditions”)
- Others
  - “Event replay”
Fundamentally:
Time-series data

---
Status Quo
- WinCC OA: de facto standard for slow controls at CERN
  - Detector/Experiment Control Systems
    - the 4 LHC detectors
    - COMPASS, NA62, protoDUNE
  - Critical infrastructure of the LHC and injectors
    - QPS, Cryogenics, Vacuum, Powering
  - Technical infrastructure
    - C&V, Electrical network, ...
- All the system use the “Oracle RDB Archiver”
  - standard component of WinCC OA
  - Highly optimized over past 15 years
    - fruit of collaboration between CERN and ETM
    - 100 v/s → 100.000 v/s

---
Experiments
ONLINE DB
OFFLINE DB
WinCC OA
Systems
(x100)
RAC
WinCC OA
Systems
(x100)
(x150)
Low latency!
Physics
Data
Analysis
ONLINE
Operation,
Monitoring

---
Accelerators and tech. infrastructure (BE/ICS Applications)
RAC
SCADAR
Long-term
storage
WinCC OA
Systems
(x100)
WinCC OA
Systems
(x100)
(x210)
LHC Logging
    (CALS)
RAC
QPSR
Low latency!
Data
Analysis
ONLINE
Operation,
Monitoring
Timber

---
Scale challenge (BE/ICS Applications)
- LHC Quench Protection System
  - 48 WinCC OA systems
  - 150k signals, 400M rows/hour insert rate
  - Dedicated Oracle instance: QPSR
  - Complete data set transmitted to ACCLOG
  - Dedicated optimizations in WinCC OA:
    for Run II of the LHC!

---
Scale challenge (BE/ICS Applications)
- “Everyone else”
  - 170 other WinCC OA systems, different clients
  - 1 DB schema per system, some correlated
  - 2.5 million signals, 34 million rows/hour insert rate
  - Share the same common online DB: SCADAR
  - Major parts of data transmitted to ACCLOG
  - Online access with minimal latency for operators
    - Trends, event screens, event replay
  - Statistics
    - how many changes per signal during last 24 hours?

---
Data analytics at the moment
RAC
SCADAR
Copy
WinCC OA
Systems
(x100)
WinCC OA
Systems
(x100)
(x210)
Data
Analytics
Daily
Statistics
Calculation
\

---
Challenging use cases of Oracle Archiver
- Three main use cases are in conflict:
  - “Trend Plot”: history of one (or few) signals
    over a possibly long period of time
    - Access through PK on IOT table, time-based partitioning
  - “Event Screen”: history of all value changes/alarms
    over relatively short period of time
    - Scan over a partition
  - “Event Replay”: massive data retrieval for all signals over a period of time of unknown bounds
    - “give me the last value before the tstart, and then all following values”
    - A killer for current Oracle setup
    - Seems significantly better executed on the Hadoop data copy

---
Why “Future Archiver”?
- ETMs motivation
  - Alternative(s) to very expensive Oracle
  - Easy to deploy and manage
  - Easy to integrate new technology
  - Lookout to NOSQL and data analytics
  - Opportunity for code cleanup
- CERNs motivation
  - IT drive to alternative(s) to Oracle
  - We face Big Data (3V)
    - Unknown limits really!
  - Enable data analytics
  - NXCALS
  - New features
    - Parallel archiving, proper treatment of meta-data history, …
    - Ready to integrate new technologies

---
Next Generation Archiver for WinCC OA
Future Archiver for WinCC OA
- Successor of Oracle RDB Archiver
  - High-performance
  - Cost-effective
  - Robustness
- Open architecture (plugins)
- SQL and NOSQL
- New architecture compatible
  with evolution of WinCC OA
[Speaker Notes: Plugin for Oracle, and other NOSQL storages]

---
Joint development with Siemens/ETM
Joint Openlab R&D projects with
Siemens/ETM and Intel/Cloudera
At CERN:
  - Piotr Golonka (technical supervision)
  - Jakub Guzik (developer of the core archiver part)
  - Rafal Kulaga (“BigData” prototype backend with Apache Kudu)
  - IT/DB coleagues (Luca, Prasanth, Zbyszek)
- At Siemens/ETM:
  - Development of the core archiver part
  - Evaluation of DB technologies
  - Oracle-compatible backend
  - MongoDB backend
  - Project ongoing since 1 year now with first prototypes becoming available
- At Intel/Cloudera: (kickoff stage)
  - Expertise for Kudu technology
    - Low latency data access
    - Quality of service and resource allocation
[Speaker Notes: One team on CERN and ETM sides]

---
High level architecture
„Frontend” and „Backend”
High level architecture
„Frontend” and „Backend”
ORACLE
Backend
Common interface =
+
„Other”
Storage
„Other”
Backend
NextGen
Archiver
In WinCC OA
Project
Big Data
Backend
Data Analytics e.g.
Streaming
Backend
Streaming as an option in the future
[Speaker Notes: Common interface for any back ends Reading (from /to WinCC OA systems) and writing interface Configuration interface to monitoring, configuring, diagnose]

---
More use cases
- “Generic data fan-out” for WinCC OA
  - Streaming data analytics
  - Data bridge for the ALICE O2
    - 100.000 conditions parameters acquired asynchronously
      (on change)
    - Most recent values need to be interleaved into the online data frames every 50 ms
    - This yields 2 mln v/s to be streamed out (!)
    - “NextGen Archiver” could provide this data
      to a custom ALICE-developed backend
      - Open architecture (!)
      - In parallel to “standard” archiving

---
Status
- Research & Development project
  - First functional prototype of complete architecture
  - Oracle, MongoDB and Kudu backend prototypes being implemented and tested
  - Baseline performance and functional tests ongoing
  - Likely to become available in a future version of WinCC OA
  - Use cases and requirements of the Experiments to be formulated, cross-checked and covered
  - Further synergies with NXCALS to be explored
  - No plans for deployment before the end of LS2