## Slide 1: Stave enclosure thermo background study
Issue:
There exists themo irregularities within the stave enclosure that should be eliminated.

## Slide 2: Stave enclosure thermo background study
Only chiller running for 6 min. No fluid flow & no stave in enclosure. Chiller set @ 20C
Chiller exhaust heats right end of enclosure.

## Slide 3: Stave enclosure thermo background study
Both chiller & booster pump running for 12 minutes. No stave in enclosure. Chiller set @ 20C
The chiller exhaust heat progress to left end of enclosure.

## Slide 4: Stave enclosure thermo background study
Both chiller & booster running for 2.5 hours. No stave in enclosure. Chiller set @ 20C
Thermo equilibrium from chiller exhaust.

## Slide 5: Stave enclosure thermo background study
2 hours after shut down of chiller & booster pump. No stave in enclosure. Chiller set @ 20C
Takes some time to recover from chiller exhaust.

## Slide 6: Stave enclosure thermo background study
Background at start. No stave in enclosure. Chiller set @ 20C
Enclosure moved to avoid chiller exhaust.

## Slide 7: Stave enclosure thermo background study
Chiller running for 35 minutes. No fluid flow. Chiller set @ 20C
Chiller exhaust has much smaller effect on right end.

## Slide 8: Stave enclosure thermo background study
Chiller & booster pump running for 56 minutes. No stave in enclosure. Chiller set @ 20C
Eventually chiller exhaust is affecting enclosure.

## Slide 9: Stave enclosure thermo background study
Chiller & booster pump running for 120 minutes. No stave in enclosure. Chiller set @ 20C
Chiller exhaust continues to heat enclosure.

## Slide 10: Stave enclosure thermo background study
45 minutes after shut down.
Again the time to recover from chiller exhaust is long.

## Slide 11: Stave enclosure thermo background study
Background at start. Stave in enclosure. Chiller set @ 20C
Stave now included in study.

## Slide 12: Stave enclosure thermo background study
Chiller & booster pump running for 50 minutes. No fluid flow. Chiller set @ 20C
Start to see warm area under stave. Right end a bit cooler.

## Slide 13: Stave enclosure thermo background study
Chiller & booster pump running for 1.5 hours. No fluid flow. Chiller set @ 20C
Chiller exhaust taking over.

## Slide 14: Stave enclosure thermo background study
Chiller & booster pump running for 2 hours. No fluid flow. Chiller set @ 20C
Chiller exhaust continues to affect.

## Slide 15: Stave enclosure thermo background study
Chiller & booster pump running for 2.83 hours. No fluid flow. Chiller set @ 20C
Equilibrium with chiller exhaust.

## Slide 16: Stave enclosure thermo background study
2.5 hours after shut down.
Again, long time to recover.

## Slide 17: Stave enclosure thermo background study
Background before start.
This run will now have cool fluid flowing through stave.

## Slide 18: Stave enclosure thermo background study
Chiller & booster started, fluid set to 10C. Fluid flow through stave. N2 gas flowing @ 12psi.

## Slide 19: Stave enclosure thermo background study
Chiller & booster pump running for 1 minute. 10C fluid flowing through stave. N2 gas flowing @ 10psi. (N2 flow decreases naturally.)
Chiller exhaust effect is too small to see.

## Slide 20: Stave enclosure thermo background study
Chiller & booster pump running for 35minutes. 10C fluid flowing through stave. N2 gas flowing @ 9psi.
Warm area appears under stave. Chiller exhaust not apparent at right end.

## Slide 21: Stave enclosure thermo background study
Chiller & booster pump running for 1.2hr with 0C fluid flowing through stave. N2 gas flowing @ 8psi.
Warm area still present under stave. Right end cool despite chiller effect. Note humidity sensor now seen.

## Slide 22: Stave enclosure thermo background study
After 1.6 hours running with 0C fluid, added Aluminum foil on end plate of enclosure near chiller. N2 gas flowing @ 7 psi.

## Slide 23: Stave enclosure thermo background study
After 1.6 hours more foil added on end of enclosure. 11” foil covered left,right,top of enclosure end. 0C fluid flowing through stave. N2 gas flowing @ 7 psi. Warm area under stave still present.

## Slide 24: Stave enclosure thermo background study
1.25 hours @ 0C fluid with 11” aluminum foil covering 3 of 4 surfaces at enclosure end. N2 gas flowing @ 7psi. Foil not improving situation.

## Slide 25: Stave enclosure thermo background study
Further work:
Start a run with foil in place at beginning.
Cover more of enclosure in foil.
Raise the enclosure off bench.
Move chiller so exhaust directed away from end of enclosure.