## Slide 1: Thermosiphon pre-design
J. Direito (EN/CV/DC)

## Slide 2: Gravity-driven Cooling Concept
Natural circulation of the fluid:
  Condensation temperature/pressure must lower than evaporation temperature/pressure
No working components in the main circuit
  Less probability of occurrence of leaks
  No significant vibrations on the system
  Low maintenance operations
Access to refrigeration units at the surface
No limit for the Evaporation Temperature:
  Suction pressure of the compressors is not a limit anymore -> possibility of reaching lower evaporation temperatures

## Slide 3: Preliminary design and parameters
A-B : Condensation
B-C : Hydrostatic dP
C-D : Heat Exchanger
D-E : Pressure Regulation
E-F : Sub-Cooling
F-G : Capillary Expansion
G-H : Evaporation
H-I : Heater
I-A : Back-Pressure regulation
B
C
D
E
G
H
I
A
F
Thermodynamic Cycle Example for C3F8 with Sub-Cooling

## Slide 4
Preliminary design and parameters
SURFACE
CAVERN
100 m
Design by A. Moraux

## Slide 5: Preliminary design and parameters
B
C
D
E
G
H
I
A
F
A-B : Condensation – dh = h (at Tcondensation) – h (at Treturn lines)
  Definition of the Condensation Power
B-C : Hydrostatic – dP > Ptransfer lines (Ttransfer lines) – Preturn lines (Treturn lines)
  Definition of minimum height
C-D : Heat Exchanger – dh = h (at Tin) – h (Tsupply lines)
  Definition of HX power
D-E : Pressure Regulation – Pressure Regulator Cv
  Regulation of mass flow
E-F : Sub-Cooling – dh = h (Tevap at Tcond) – h (Xin)
  Definition of HX Power for sub-cooling
F-G : Capillary pressure drop – dP = Ppressure regulator – Pevaporation
  Definition of capillary length
G-H : Evaporation – dP stave
  Definition of dP at the stave
H-I : Heater – dh = h (Xout) – h (Ttransfer lines)
  Definition of Heater power
I-A : Back-Pressure regulation – Pressure Regulator Cv
  Regulation of Evaporation Temperature

## Slide 6: Preliminary design and parameters
Application example for the IBL detector and Distribution Racks at USA 15:
  Required mass flow = 36g/s
  Evaporation temperature = -40C
  Supply and return lines Temperature = 20C
  Altitude difference ≈ 100m
Definition of the main components:
  Minimum height O.K.: 16 bar > dP (Pcond = 7.57 bar ; Pevap = 0.87 bar)
  liquid line = DN25 -> dP= 16 bar ; Vapor line = DN50 -> dP = 90 mbar
  Condensation Temperature < -42.5 C (Pcond < 0.87 bar – 90mbar)
  Condenser Power > 5.94kW (dh = 165kJ/kg; m = 36g/s)
  Heat Exchanger Power > 1.44kW (dh = 40kJ/kg; m = 36 g/s)