## Slide 2: Powering tests after 16/17 EYETS
M. Solfaroli and M. Pojer
On behalf of all teams involved in the powering tests
19/04/2017

## Slide 3: Preparation status
ElQA is completed
Cable connected everywhere
Power converters de-condemned everywhere
EE released everywhere
QPS-IST missing on few circuits
DONE
DONE
DONE
DONE
DONE
DONE
To be done today
To be done today

## Slide 4: General
Many 60 A PNO.a1 are failing on a “high resistance” error: not clear whether the measurement is more precise with the new FGC lite or there is an error in the value used for the analysis
Several PIC and PNO.d1 spread across the machine have to be signed in the ACCTESTING by MP3 and EPC
Some specific issues sent directly to Reiner:
  QPS_DCCT saturated for some RSD/F circuits (jumps at 590A)
  Drift of I_DCCT for few circuits - tight some bolts?
To be done:
  Calibration of high current circuits DCCT – tomorrow p.m.
  Test on 1 converter per type with new FGC-lite in one RR to be planned
  Test of water interlock stopping water pumps in all sectors
    RQ8.L8B1 eletta to be replaced today
  Internal splice measurements in 9 positions in S12 (after commissioning, with ElQA support)
  RCS.A78B2 and RCO.A78B1: fault localization when powering Mains
  Conical joint measurement in UA27, with prototypal installation (issues after LS1)

## Slide 5: IPQ inversion
 | Powered | Checked by QPS
RQ4.R2 | Y | Y
RQ8.R2 | Y | Y
RQ9.R2 | Y | Y
RQ10.R5 | Y | Y
RQ9.R5 | Y | Y
RQ5.R8 | Y | Y
RQ7.R8 | Y | Y
RQ8.R8 | Y | Y
RQ9.R8 | Y | Y
Inversions of aperture identified during powered and corrected:
(several circuits still to check!)

## Slide 6: Phase II powering permits
Only S12 and S23 are missing and will be released after the UPS test

## Slide 7: MAINS

## Slide 8: XR1
RQX.R1: QH discharge to be looked at by MP3
Quenched due to bad cooling
Blocked by Cryo

## Slide 9: LR1
RQ6.R1 was stalled after the PIC2-circuit quench and had to be reset
MP3 and EPC signatures for the 120 A and RQ6.R1

## Slide 10: ARC12
Just started…
PCC done on the Mains and ongoing on the IPQs
PIC2 done on the 600 A
ROF.A12B2 and RQTF.A12B2 blocked by cryo
RCBCH10.L2B2 has an offset on U_Lead_pos and it is failing the automatic analysis

## Slide 11: ML2
RCBYVS5.L2B2 had an earth fault during test, but could be reset: EPC to check!
U_lead_neg has offset

## Slide 12: XL2
Ongoing

## Slide 13: XR2 and MR2
Waiting for Phase II
T regulation
MP3 to sign

## Slide 14: ARC23
Waiting for Phase II
4x60 A failed because of “high resistance”
“High resistance”
“High resistance”
“High resistance”
“High resistance”

## Slide 15: ARC34
PNO test failed on the quads during ramp-down: QPS to analyze and fix
EPC sign.
“High resistance”
“High resistance”
In MQ23.R3, heaters fired during the ramp-down: QPS to advice!

## Slide 16: ML4 and MR4
Completed

## Slide 17: ARC 45
RB and some IPQs not yet available
13 x 60 A failed due to “high resistance”
EPC and Mp3 to sign
EPC and MP3 to sign
large sigma_U_diff
(155 mV vs 5 mV)

## Slide 18: LL5
IPQs and IPD not yet available

## Slide 19: XL5
IT not yet available
T regul not OK
T regul not OK
T regul not OK
T regul not OK
T regul not OK
T regul not OK

## Slide 20: XR5
IT not yet available
T regul not OK
T regul not OK
T regul not OK
T regul not OK
T regul not OK
T regul not OK

## Slide 21: LR5
Completed

## Slide 22: ARC56
RQTL11.R5B1: 0-V crossing
RQTL11.R5B1: training quench at 482 A, 1 QPS file missing
RQTL11.R5B2 : 0-V crossing
MP3 sign.
MP3 and EPC to sign
Large U_res
Train@482A + 0V-crossing
0V-crossing
MP3 sign.
MP3 sign.
MP3 sign.
MP3 sign.
PC in FLT_OFF

## Slide 23: ML6 and MR6
Completed

## Slide 24: ARC 67
Few IPQs not yet available
RQT12.L7B2 = DC CONTACTOR FAULT at startup (intervention required)
RSF1.A67B1: breaker B replacement needed; agreed for this morning

## Slide 25: ARC 78
~40 x 60 A with “high resistance”
RQTL9.R7B2: 0-V crossing
I_earth overcurrent!
Large U_res
Large U_res

## Slide 26: ML8
Completed

## Slide 27: XL8
IT not yet available
T regul not OK
T regul not OK
T regul not OK
T regul not OK
T regul not OK
T regul not OK

## Slide 28: XR8 and MR8
T regul not OK
T regul not OK
T regul not OK
T regul not OK
T regul not OK
T regul not OK
MP3 sign.

## Slide 29: ARC81
MP3 to sign
MP3 to sign
Large U_res
T oscillations
“High resistance”
MP3 to sign

## Slide 30: LL1
Completed

## Slide 31: XL1
T regul not OK
T regul not OK
T regul not OK
T regul not OK
T regul not OK
T regul not OK
T regul not OK