## Slide 1
EP EXSO Meeting
Emergency Stop
Electrical Inspection
Gilles MAIRE EP/DI-SO
EP Electrical Safety Officer (ESO)

## Slide 2
Outline
Emergency Stop
Reminder Emergency Stop at CERN.
AUL test in January 2017.
Consolidation Plan.
Electrical Inspection
Motivation.
Request for an Inspection.
Organization.

## Slide 3
Reminder about Emergency Stop at CERN
AUG (General Emergency Stop)
Installed in accelerator building, experimental hall, etc. In case of AUG, cut off all experiments, beams.
Cut off all power sources, except the equipment's supplied by the uninterruptible power supply.
Level 3 alarm (Fire Brigade).
EN/EL responsibility, tested yearly.
AUL (Local Emergency Stop)
Installed in areas clearly demarcated. In case of AUL, cut off only the concerned experiment.
Cut off all power sources in the concerned experiment, except the equipment's supplied by the uninterruptible power supply.
EXSO TSO responsibility, tested yearly with help of EP safety office.
AUE (Equipment Emergency Stop)
AUE stop only the associated equipment.
Responsibility of owners equipment.

## Slide 4
AUL test in January 2017
Motivation
No documentation available. Make an inventory of AULs.
Test the functionality of AULs.
Verify the cut-off of circuit breakers feeding the equipment.
Propose a consolidation plan if needed.
Results
Too many AUL in certain experiment, no AUL in other experiment.
Some AULs are not visible or accessible.
AULs do not cut-off all concerned equipment.
Conclusion
AULs do not protect correctly the safety of persons.
Propose a consolidation plan.
Experiments concerned
AD. Isolde.
North and East Area.

## Slide 5
AUL Consolidation Plan
No Consolidation Plan
GIF++
CLOUD
ISOLDE
Experiments concerned by the Consolidation Plan
NA61 during the YETS 2017-2018
AD experiments during the YETS 2017-2018
COMPASS during the YETS 2017-2018
T9 and T10 during LS2

## Slide 6
Electrical Inspection
Motivation
Electrical nonconformities. Grounding, direct contact, HV, etc…
Organization
Electrical Inspection done by HSE in collaboration with EP ESO.
HSE EDMS Report with nonconformities.
Modification by the experiment.
New visit to validate modification (HSE & ESO).
Request for an Inspection
New experiment, asked by the EXSO.
Modification or new electrical equipment installed, asked by the EXSO.
May also be requested by the Safety Office.

## Slide 7
Summary
In case of doubt about your electrical installation.
In case of new electrical equipment on your experiment.
In case of problem with AUL or AUG.
Don’t hesitate to contact your Safety Correspondent OR EP Electrical Safety Officer.