## Slide 1: LHC beam screens: cryogenic observations and analysis
Benjamin Bradu,
Krzysztof Brodzinski and Serge Claudet
TE-CRG
E-cloud meeting
14th July 2017

## Slide 2: Contents
Heat load observations in ARCS
Evolution of Feed-Forward parameters
Heat load observations in instrumented cells
Notes: 2

## Slide 3: ARC Heat loads 2016 Vs 2017
S12
S23
S34
S45
S56
S67
S78
S81
Fill #5416 = 14th October 2016: 25ns_2220b_2208_1940_2036_96bpi_24inj
Fill #5882 = 28th June 2017: 25ns_2556b_2544_2215_2332_144bpi_20inj

## Slide 4: ARC Normalized Heat loads 2016 Vs 2017
S12
S23
S34
S45
S56
S67
S78
S81
Fill #5416 = 14th October 2016: 25ns_2220b_2208_1940_2036_96bpi_24inj
Fill #5882 = 28th June 2017: 25ns_2556b_2544_2215_2332_144bpi_20inj

## Slide 5: Feed-Forward: Reminder
Feed-forward action on cryo valves + heaters to anticipate heat loads
Beam induced heat load calculated from online beam parameters
3 tuning parameters are used to compute the e-cloud contribution :
  Qeci: heat load per half-cell per bunch at injection (450 GeV)
  Qecr: heat load per half-cell per bunch after ramp (6.5 TeV)
  Nb0: proton per bunch threshold to activate e-cloud process

## Slide 6: Heat Load observations in ARC
Evolution of FF parameters
  Qeci: heat load per half-cell per bunch at injection (450 GeV)
Chart: Qeci
| 12 | 23 | 34 | 45 | 56 | 67 | 78 | 81
Fill 5416 | 0.032223 | 0.030022 | 0.010693 | 0.015582 | 0.016652 | 0.014254 | 0.023108 | 0.038747
Fill 5882 | 0.032179 | 0.030738 | 0.011186 | 0.016382 | 0.017601 | 0.014584 | 0.023491 | 0.039616
Fill #5416 = 14th October 2016: 25ns_2220b_2208_1940_2036_96bpi_24inj
Fill #5882 = 28th June 2017: 25ns_2556b_2544_2215_2332_144bpi_20inj
Conditioning finished at 450 GeV

## Slide 7: Heat Load observations in ARC
Chart: Qecr
| 12 | 23 | 34 | 45 | 56 | 67 | 78 | 81
Fill 5416 | 0.042886 | 0.039449 | 0.015244 | 0.019913 | 0.021225 | 0.018867 | 0.033426 | 0.046648
Fill 5882 | 0.05257 | 0.039776 | 0.013737 | 0.019515 | 0.02116 | 0.02004 | 0.034631 | 0.046826
Evolution of FF parameters
  Qecr: heat load per half-cell per bunch after ramp (6.5 TeV)
Fill #5416 = 14th October 2016: 25ns_2220b_2208_1940_2036_96bpi_24inj
Fill #5882 = 28th June 2017: 25ns_2556b_2544_2215_2332_144bpi_20inj
Conditioning not yet finished at 6.5 TeV

## Slide 8: Heat Load observations in ARC
Chart: Nb0
| 12 | 23 | 34 | 45 | 56 | 67 | 78 | 81
Fill 5416 | 36949465229.1469 | 38701588148.3819 | 36600793960.3705 | 35574645158.0193 | 43305582755.9538 | 49540197381.0045 | 41204164360.4999 | 36264315569.0817
Fill 5882 | 24281496021.1328 | 25502181416.8182 | 34650217284.1549 | 26379220765.2053 | 39579142910.1626 | 56022732743.2699 | 30382738823.9016 | 16772231495.7545
Evolution of FF parameters
  Nb0: proton per bunch threshold to activate e-cloud process
Fill #5416 = 14th October 2016: 25ns_2220b_2208_1940_2036_96bpi_24inj
Fill #5882 = 28th June 2017: 25ns_2556b_2544_2215_2332_144bpi_20inj
E-cloud threshold slightly lower after EYETS in high load sectors (12,23,78,81)

## Slide 9: E-cloud threshold in ARC12
Nb0 =
3.69e10
Nb0 =
2.43e10
Qec = Qdbs (meas) - Qsr (theo) – Qic (theo)

## Slide 10: E-cloud threshold in ARC81
Nb0 =
3.63e10
Nb0 =
1.68e10
Qec = Qdbs (meas) - Qsr (theo) – Qic (theo)

## Slide 11: Instrumented cells
3 cells in S45 since LS1
1 cell in S12 since EYETS 2016
Total = 4 quadrupoles and 12 dipoles
Before EYETS 2016:
  34R4: one sensor not working (QBBI_A34L5_TT826)
  34R4: suspicious sensor (QBBI_A34L5_TT824)  Error on 2 dipoles
  13L5: sensor calibration issues  Errors on 1 quadrupole
After EYETS 2016
  All sensors have been re-calibrated
  34R4: Previous issues solved except QBBI_A34L5_TT824 still suspicious
  13L5: One sensor not working (QBBI_B13L5_TT824)
   all magnet heat loads can be correctly calculated in 2017

## Slide 12: Instrumented cells in S45
Suspicious
(2016-2017)
Not working
(2016)
Not working (2017)
Suspicious (2016)
 very good temperature matching between B1/B2 between 6 K/30 K : no sensor deviation

## Slide 13: Instrumented Quadrupoles
12R4
34R4
13L5
31L2
Instrumentation
issue in 2016
No instrumentation
in 2016
Fill #5416 @ 6.5 TeV (14th October 2016) 25ns_2220b_2208_1940_2036_96bpi_24inj
Fill #5821 @ 450 GeV (12th June 2017) 25ns_2820b_288bpi_scrub2017
Fill #5882 @ 6.5 TeV (28th June 2017) 25ns_2556b_2544_2215_2332_144bpi_20inj
ARC12
Average
Fill #5882
ARC45
Average
Fill #5882

## Slide 14: Instrumented Dipoles
Fill #5416 @ 6.5 TeV (14th October 2016) 25ns_2220b_2208_1940_2036_96bpi_24inj
Fill #5821 @ 450 GeV (12th June 2017) 25ns_2820b_288bpi_scrub2017
Fill #5882 @ 6.5 TeV (28th June 2017) 25ns_2556b_2544_2215_2332_144bpi_20inj
12R4
34R4
13L5
31L2
No instrumentation
in 2016
Replaced dipole
during EYETS
Instrumentation issue
in 2016 for 2 dipoles
ARC12
Average
Fill #5882
ARC45
Average
Fill #5882

## Slide 15: Conclusion
Heat loads in ARC
  2017 similar to 2016
  S12 conditioning done @ 450 GeV, not yet @ 6.5 TeV
FF parameters
  2017 similar to 2016 except for e-cloud threshold (small impact)
Instrumented cells
  Quadrupoles
    “heating” at injection (450 GeV)
    Small dispersion of quadrupole heat loads at 6.5 TeV (but only 4 quad)
  Dipoles
    “heating” after the ramp (6.5 TeV)
    Important dispersion of dipoles at 6.5 TeV (on 12 dipoles)
  Replaced Dipole in 31L2 shows lower heat loads than the rest of S12

## Slide 16: Beam screen heating – 2017
From K.Brodzinski_TETM_2017.06.22: https://indico.cern.ch/event/633648/