## Slide 2: Performance Based Safety Design and results on Cryogenic hazards
André Henriques, Saverio La Mendola
FCC Week 2018
Amsterdam, NL
Thanks to the FCC I&O WG members

## Slide 3
Introduction
1
Performance Based Design
2
Cryogenic Safety studies (FCC-hh)
3
Outline
Conclusions
4

## Slide 4: Introduction
Legislative references are NOT applicable
Legislative references are applicable
Project Safety
Requirements
‘Standard Best Practices’
SBP
‘Performance Based Design’
PBD
Ex:
Egress
routes
35 m
6.5-9.5 km
Automatically conform, without additional measures
Adaptation & additional measures needed
500 m*
*see spare slide
Notes: 35 to 10000 m is a factor ~300 (3 orders of magnitude)
Road tunnels is 500m

## Slide 5: Introduction
Hazard Register
FCC Hazard Register:
Systematic collection of Hazards in the FCC facilities during different phases of its lifetime
No assessment of probability or severity
SBP
PBD
Impact for FCC CDR
e.g.
Cryogenic; Fire
Thursday 08:55: Fire safety assessment for FCC (O. Rios)
T. Otto
…
Database
H1
H2
H3
H4
H5
H6
H7
H8
H9
H10
H11
H12
H13
H14
H15
H16
Hn

## Slide 6: Performance Based Design
Safety Goals
Safety Objectives
Accidental Scenarios
Trial Design
Evaluation
Meets Objectives
New trial design
Additional measures
Performance criteria
Notes: Requirements of the project
(domain independent)

## Slide 7: Performance Based Design
Safety Goals
Defined by Organizations' Safety Policy
Notes: Requirements of the project
(domain independent)

## Slide 8
Safety Goals
CERN’s Safety Policy
Occupational Health and Safety
Workers
Visitors
Neighbours
…
Protection of the envronment
Air
Water
Soil
…
Equipment and Operation
Unsafe operation
Property protection
Downtime
…
VISITOR
Priority
Safety Goals:
Occupational Health & Safety
Environmental Protection
Property Protection
Continuity of Operation
Independent of the Safety domain / project

## Slide 9: Performance Based Design
Safety Goals
Safety Objectives
Defined by Organizations' Safety Policy
Requirements of the project
i.e. Applicable Rules
Notes: Requirements of the project
(domain independent)

## Slide 10: Safety Objectives – FCC Study
 | Occupational Health and Safety | Environmental protection | Property protection | Continuity of operation
 | A | B | C | D
1 | Occupants shall be able to evacuate through protected areas, free from smoke/gas and other hazards at any time | Limit the release of polluting (incl. activated) agents to the environment in case of incident | The continuity of essential services and structural stability is assured in case of fire or gas release and other incidents | Limiting the downtime in case of incident
2 | Victims and other occupants, not able to self-evacuate, shall reach protected areas, and wait there to be rescued by the intervention teams | Limit the volume of polluted (incl. activated) water released to the environment in case of incidents | An incident shall not cause other potentially dangerous accidental events | -
3 | Rescue teams shall be able to intervene safely and according to current CERN SOPs | - | Limiting the property loss in case of incident | -
Notes: (e.g. in case of major release, replacing damaged equipment)

## Slide 11: Safety Objectives – FCC Study
 | Occupational Health and Safety | Environmental protection | Property protection | Continuity of operation
 | A | B | C | D
1 | Occupants shall be able to evacuate through protected areas, free from smoke/gas and other hazards at any time | Limit the release of polluting (incl. activated) agents to the environment in case of incident | The continuity of essential services and structural stability is assured in case of fire or gas release and other incidents | Limiting the downtime in case of incident
2 | Victims and other occupants, not able to self-evacuate, shall reach protected areas, and wait there to be rescued by the intervention teams | Limit the volume of polluted (incl. activated) water released to the environment in case of incidents | An incident shall not cause other potentially dangerous accidental events | -
3 | Rescue teams shall be able to intervene safely and according to current CERN SOPs | - | Limiting the property loss in case of incident | -
Occupants
Victims
Rescue teams
Env. impact
Property loss
Downtime
Notes: (e.g. in case of major release, replacing damaged equipment)

## Slide 12: Safety Objectives – FCC Study
 | Occupational Health and Safety | Environmental protection | Property protection | Continuity of operation
 | A | B | C | D
1 | Occupants shall be able to evacuate through protected areas, free from smoke/gas and other hazards at any time | Limit the release of polluting (incl. activated) agents to the environment in case of incident | The continuity of essential services and structural stability is assured in case of fire or gas release and other incidents | Limiting the downtime in case of incident
2 | Victims and other occupants, not able to self-evacuate, shall reach protected areas, and wait there to be rescued by the intervention teams | Limit the volume of polluted (incl. activated) water released to the environment in case of incidents | An incident shall not cause other potentially dangerous accidental events | -
3 | Rescue teams shall be able to intervene safely and according to current CERN SOPs | - | Limiting the property loss in case of incident | -
Occupants
Victims
Rescue teams
Env. impact
Property loss
Downtime
Independent on the Safety Domain !
Notes: (e.g. in case of major release, replacing damaged equipment)

## Slide 13: Performance Based Design
Safety Goals
Safety Objectives
Performance criteria
Defined by Organizations' Safety Policy
Requirements of the project
i.e. Applicable Rules
Measurable requirements
i.e. Harmonized Standard
Notes: Requirements of the project
(domain independent)

## Slide 14: Performance criteria
Quantitative
Threshold
values
Qualitative
Performance
goals
- Presence of toxic smoke shall not influence the evacuation of occupants
Exposure to :
FED < 0.1 (e.g.)
Exposure temperature < 60oC (e.g.)
Visibility > 10 m (e.g.)
- Helium cloud shall not reach the compartment door before the occupant evacuating
Exposed to:
O2 level > 18 %
Vventilation < Vwalking = 1.2 m/s
CDR
TDR
Technical specification can also become performance criteria
Notes: Technical design spec: e.g. pressure SRF limited to a low PS

## Slide 15: Performance Based Design
Safety Goals
Safety Objectives
Accidental Scenarios
Performance criteria
Defined by Organizations' Safety Policy
Requirements of the project
i.e. Applicable Rules
Measurable requirements
i.e. Harmonized Standard
List of scenarios based on Risk Assessment
Notes: Requirements of the project
(domain independent)

## Slide 16: Performance Based Design
Safety Goals
Safety Objectives
Accidental Scenarios
Trial Design
Performance criteria
Defined by Organizations' Safety Policy
Requirements of the project
i.e. Applicable Rules
Measurable requirements
i.e. Harmonized Standard
List of scenarios based on Risk Assessment
First iteration with initial specification
Notes: Requirements of the project
(domain independent)

## Slide 17: Trial Design
FCC-hh
Baseline includes Safety features
F. Valchkova-Georgieva

## Slide 18: Performance Based Design
Safety Goals
Safety Objectives
Accidental Scenarios
Trial Design
Evaluation
Meets Objectives
New trial design
Additional measures
Performance criteria
Defined by Organizations' Safety Policy
Requirements of the project
i.e. Applicable Rules
Measurable requirements
i.e. Harmonized Standard
List of scenarios based on Risk Assessment
First iteration with initial specification
Measured against the safety objectives (iterative process)
Notes: Requirements of the project
(domain independent)
Binary evaluation

## Slide 19: Evaluation
Consequences are described on a qualitative basis
(e.g. egress possible, compartments doors open/close)
Qualitative
Same as above but consequences are quantified
(e.g. smoke/He propagation, damage to equipment, etc.)
Quantitative
Consequences and probabilities of scenarios are quantified and their combination evaluated in a risk matrix
Probabilistic
Every scenario is evaluated through risk profiles and other risk indicators.
Full Probabilistic
CDR
TDR
Probabilistic
Deterministic

## Slide 20: Performance Based Design
Safety Goals
Safety Objectives
Accidental Scenarios
Trial Design
Evaluation
Meets Objectives
New trial design
Additional measures
Performance criteria
Defined by Organizations' Safety Policy
Requirements of the project
i.e. Applicable Rules
Measurable requirements
i.e. Harmonized Standard
List of scenarios based on Risk Assessment
Measured against the safety objectives (iterative process)
First iteration with initial specification
Trial Design is valid
Notes: Requirements of the project
(domain independent)

## Slide 21: Cryogenic Safety studies – FCC-hh
Based on contributions from the FCC PBD Working Group

## Slide 22: Input Data
Air/He velocity in the tunnel
  Nominal: 0.3 m/s
  For the first 100s seconds after a helium release, downstream: 0.7 m/s
Helium inventory:
  Superconducting magnets: 33 l LHe / m
  Cryogenic ring line (QRL): 49 l supercritical He / m*
Helium sectorisation:
  Superconducting magnets: 220 m (corresponding to 1 cell)
  Cryogenic ring line (QRL): 8400 m (corresponding to sub-sector)
Gaseous helium inventory
  Superconducting magnets: 1 t
  Cryogenic ring line (QRL): 22 t
* header E
M.Nonis, G. Peon, L. Tavian
+ LHC
studies

## Slide 23: Input Data
Distance from a helium release in the tunnel that can be detected by human senses (sight or hearing): ~150 m
2 ODH detectors per compartment
Notes: 150 m Note: important assumption – further studies needed
LHC have ODH detector every 300m

## Slide 24: Input Data
Δtdet = distance to ODH detector / He cloud prop. velocity
Δta = 5s
Δtpre = 30 s *
Δttra = walking speed x evac. distance
walking speed = 1.2 m/s
Evacuation time (according to British Standard PD 7974-6 ):
* Occupants are properly familiar with the underground layout and trained to a high level of safety management
Release point is next to one door
Evacuation is made downstream
Occupant doesn’t stop to put on SRM

## Slide 25: Release scenarios
MCI* (design)  ~ 30 kg/s
Relief plate release  ~ 1 kg/s
Small leak  ~ 300 g/s
Minor leak  ~ 100 g/s
Based on LHC data
Note: No detailed studies yet made for FCC cryostats
*Maximum Credible Incident

## Slide 26: Accidental scenarios
Scenario | Description
Cryo1 | 1 kg/s ; 5 m from release point
Cryo2 | 1 kg/s ; 5 m from release point; emergency extraction ON
Cryo3 | 1 kg/s ; 200 m from release point
Cryo4 | 0.3 kg/s; 150 m from release point
Cryo5 | 0.1 kg/s; 5 m from release point
Cryo6 | 32 kg/s during operation
Varying the relief mass flow & distance to the release

## Slide 27: Evaluation of the Trial Design
Summary
Based on simplified model

## Slide 28: Cryo1: 1 kg/s ; 5 m from release point
d = 0
440
Fire door open
t=390s
160
[m]
Time lapse after release (d=5m)
Fire door open
d = 0
440
t=40s
30
[m]
20
‘Turbulent Zone’ – non-stay areas
‘Stratified Zone’
Illustrations are not to scale
Critical distance in the ‘Turbulent zone’
Notes: Overtake the cloud after 2min

## Slide 29: Cryo2: 1 kg/s ; 5 m from release point; extraction ON
t = [5, 10] min  The extraction is ON @ full capacity
Cloud propagation stops after 220 m
After passing 2 fire doors (880m) is considered ‘safe’ to wait for transportation
He ext. ON
Wednesday 13:30: Development for cooling and ventilation systems (M. Nonis; G. Peon)
Notes: 10 min is based on the time to “suck” all the air in a 5 km duct (8min) and to start up the ventilator
Flow rate of 20 000 m3/h

## Slide 30: Cryo4: 0.3 kg/s ; 150 m from release point
Illustrations are not to scale
Time lapse after release (d=150m)
d = 0
440
t=400s
160
Door open
[m]
150
Less mass flow = smaller GHe layer  t.b.c via CFD

## Slide 31: Cryo4: 0.3 kg/s ; 150 m from release point
Illustrations are not to scale
Time lapse after release (d=150m)
d = 0
440
t=400s
130
Door open
[m]
150
Critical distance for this exercise is the ‘acknowledgment limit’ of the warning signs
He extraction ON after 5 min
He extraction critical
Innovative emergency evacuation signs
Thursday 09:20: Virtual reality experiments for evacuation in the FCC (S. Arias)

## Slide 32: Evaluation of Trial design - FCC
 | Trial design #1 |  |  |  |  |  |  |  | 
Accidental Scenarios | Health & Safety of personnel |  |  | Environmental protection |  | Property protection |  |  | Continuity of operations
 | A1 | A2 | A3 | B1 | B2 | C1 | C2 | C3 | D1
Cryo1 | X | X | X(?) |  |  |  |  |  | 
Cryo2 | X (?) | X |  (?) |  |  |  |  |  | 
Cryo3 |  | X | X(?) |  |  |  |  |  | 
Cryo4 |  | X (?) |  |  |  |  |  |  | 
Cryo5 |  |  |  |  |  |  |  |  | 
Cryo6 | X | X | X |  |  |  | X | X | X

## Slide 33: Evaluation of Trial design - FCC
 | Trial design #1 |  |  |  |  |  |  |  | 
Accidental Scenarios | Health & Safety of personnel |  |  | Environmental protection |  | Property protection |  |  | Continuity of operations
 | A1 | A2 | A3 | B1 | B2 | C1 | C2 | C3 | D1
Cryo1 | X | X | X(?) |  |  |  |  |  | 
Cryo2 | X (?) | X |  (?) |  |  |  |  |  | 
Cryo3 |  | X | X(?) |  |  |  |  |  | 
Cryo4 |  | X (?) |  |  |  |  |  |  | 
Cryo5 |  |  |  |  |  |  |  |  | 
Cryo6 | X | X | X |  |  |  | X | X | X
(?)  Cannot be determined with 100% certainty, due to the lack of data (simulations/studies are needed)

## Slide 34: Evaluation of Trial design - FCC
 | Trial design #1 |  |  |  |  |  |  |  | 
Accidental Scenarios | Health & Safety of personnel |  |  | Environmental protection |  | Property protection |  |  | Continuity of operations
 | A1 | A2 | A3 | B1 | B2 | C1 | C2 | C3 | D1
Cryo1 | X | X | X(?) |  |  |  |  |  | 
Cryo2 | X (?) | X |  (?) |  |  |  |  |  | 
Cryo3 |  | X | X(?) |  |  |  |  |  | 
Cryo4 |  | X (?) |  |  |  |  |  |  | 
Cryo5 |  |  |  |  |  |  |  |  | 
Cryo6 | X | X | X |  |  |  | X | X | X
X  To be mitigated by organisational measures (e.g. access restrictions, non-stay areas, accept property loss)
Full Report EDMS N. 1818330
(?)  Cannot be determined with 100% certainty, due to the lack of data (simulations/studies are needed)

## Slide 35: Conclusions
PBD is very useful as Risk Assessment method for non-standard installations  used for FCC CDR
Trial Design (with safety features) fulfils the majority of the Safety Objectives
Unfulfilled objectives can be mitigated by organisational measures
  No affect on the infrastructure of the FCC tunnel
  Baseline FCC cross-section is acceptable
A more qualitative evaluation shall be carried out at a TDR level
  Transportation system in case of evacuation
  Studies on the height of the helium gas layer (CFD simulations)
FCC-ee & HE-LHC studies are ongoing and will be ready for the CDR
Notes: Cryo 4 against objective A1; A2 need to be further studied.

## Slide 36
Thank you very much
for your attention
Acknowledgements:
S. La Mendola, V. Mertens, T. Otto, S. Marsh, M. Nonis, O. Rios, J. Osborne, L. Tavian, S. Grau, G. Lindell, G. Peon, M. Widorski, FCC I&O WG memebrs

## Slide 38: Spare slides

## Slide 39: Evacuation distance in road tunnels
EU Directive 2004/54/EC on minimum safety requirements for tunnels in the Trans-European Road Network
“Where emergency exits are provided, the distance between two emergency exits shall not exceed 500 m.”
Manuel AIPCR des tunnels routiers
L’Association mondiale de la Route (AIPCR), Manuel des tunnels routiers
“L’inter distance optimale entre deux issues de secours résulte de l’Analyse des Risques.”

## Slide 40: Case study: Quantitative deterministic evaluation
Main assumptions (e.g.):
ventilation velocity;
length of detection zone;
When ventilation on, He propagates with the ventilation velocity;
When ventilation off, He propagates due to buoyancy
Based on these assumptions we can calculate:
He propagation downstream;
He propagation upstream;
Total tunnel length interested by He
estimated downtime cost;
Other quantities can be calculated: gas temperature, O2 levels, visibility, etc.
Courtesy of S. La Mendola

## Slide 41: Case study: Probabilistic evaluation
Estimated total cost of an accidental scenario.
It was chosen because considered likely.
We can now try to estimate quantitatively its likelihood through a probability calculation.
Assumptions (e.g.):
20% of lifetime the facility is expected to be in shutdown;
10% of shutdown there will be works in arcs;
The probability of having a He release caused by works [10-x /d];
ODH detection and actions (alarm and ventilation off) work as foreseen;
Calculate probability (Poisson process) for this scenario;
The expected cost (risk) is Estimate_cost * Poisson_prob [kCHF/y]
Consequences and probabilities can be used to locate this scenario in a risk matrix.
Courtesy of S. La Mendola

## Slide 42: Case study: Probabilistic evaluation. Risk matrix (adapted from SFPE guide)
Description of Consequence
Negligible: Minimum damage to building, minimal operational downtime;
Low: Damage < CHFyy value, reparable damage to building, significant operational downtime, no impact on surroundings;
Moderate: CHFyy < damage < CHFxx, major equipment destroyed, minor impact on surroundings
High: Damage > CHFxx, building destroyed, surrounding property damaged.
Description of Frequency – SFPE approach
Anticipated, expected: incidents that might occur several times during the lifetime of the facility (f > 10-2/y);
Unlikely: events that are not anticipated to occur during the lifetime of the facility (10-4/y < f ≤ 10-2/y);
Extremely unlikely: events that will probably not occur during the life cycle of the facility (10-6/y < f ≤ 10-4/y);
Beyond extremely unlikely: all other incidents (f > 10-6/y).
The star indicates the position of the scenario (example)
Courtesy of S. La Mendola

## Slide 43: Case study: Probabilistic evaluation.
Scenarios can be seen as a particular path in an event tree:
Event tree: tunnel arc - long shutdown phase – ignition due to hot work
Ignition due to hot work P(IHW)
 | Extinction by Occupants (E) | Fire Detection (D) | Sound Alarm (A) | Ventilation stops (V) | Scenario ID | Prob. / y | Consequence [kCHF] | Expected cost [kCHF/y]
 |  |  |  |  | 1 | … | … | …
 |  |  |  |  | 2 | 10-x | y | y * 10-x
 |  |  |  |  | 3 | … | … | …
 |  |  |  |  | 4 | … | … | …
 |  |  |  |  | 5 | … | … | …
 |  |  |  |  | 6 | … | … | …
 | Extinction by Occupants (E) | Fire Detection (D) | Sound Alarm (A) | Ventilation stops (V) | Scenario ID | Prob. / y | Consequence [kCHF] | Expected cost [kCHF/y]
 |  |  |  |  | 1 | … | … | …
 |  |  |  |  | 2 | 10-x | y | y * 10-x
 |  |  |  |  | 3 | … | … | …
 |  |  |  |  | 4 | … | … | …
 |  |  |  |  | 5 | … | … | …
 |  |  |  |  | 6 | … | … | …
Courtesy of S. La Mendola

## Slide 44: Case study: fire in the arc of a generic accelerator tunnel during a long shutdown. Full probabilistic evaluation.
Consequence kCHF
Probability /y
10-1
10-2
10-3
10-4
10-5
10-6
10-7
10-8
102
103
104
105
10
1
10-9
If the risk profile of a project:
is above the upper ALARP curve, the design solution is unacceptable;
is below the lower ALARP curve, the design solution is acceptable;
If the risk profile of a project lies between the upper and the lower ALARP curves, a cost – benefit analysis should be made.
Unacceptable
Acceptable
Cost – Benefit analysis
If C is the total cost of fire protection measures and CF is the expected fire loss, the optimum design minimizes:
CT = C + CF
CT = C + CF
CF
C
C
Courtesy of S. La Mendola

## Slide 45: Cryo3: 1 kg/s ; 200 m from release point
Propagation of He cloud and evacuation distance
Occupant is always ‘ahead’ the He cloud
Δtpre

## Slide 46: Cryo6: : 32 kg/s during operation
Sectorise the He inventory each 2 half-cells ~ 220m
33 l LHe / m  7260 l LHe
@ 300 K  ~ 1 ton GHe
Fire compartment: 440 m
5.5 m Ø : 15 m2
5.5 m Ø  7000 m3 of air + 5 600 m3 GHe
 1300 mbar pressure increase
With doors closed
CFD calculation needed…
With doors open
Property protection
Loss of one compartment & 1 cell
Downtime
1 year of operation
L. Tavian