## Slide 1: Introduction to Energy & Power Conversion
Greek Teachers Programme 2018
Konstantinos Papastergiou | Technology Department
CERN – European Organisation for Nuclear Research

## Slide 2
το CERN στα μάτια μας

## Slide 3
cern
100 searches
16
10
2008 only

## Slide 4
1897
Ανακάλυψη ηλεκτρονίου
Nobel 1906, Joseph John Thomson, Cambridge Cavendish Laboratory

## Slide 5: Summary
Energy consumption at CERN
  How is energy used?
  Electricity, Water and Gas
From Electrical to Kinetic Energy
  How is electricity converted to acceleration?
Key electrical consumers?
  Components with power requirements
Electronics and Power Electronics
  What is the difference
Power Conversion Principle
  Why and how is energy converted
Accelerator Power Electronics
  Real world systems – how do they look
Research Challenges
  The future in powering accelerators

## Slide 6
CERN και ενέργεια

## Slide 7: Electricity at CERN
Interconnections to both France and Switzerland
Approximately 80% of electricity from France
  French Energy mix: 75%Nuclear,16% Hydro, Thermal 9%
1000 high voltage circuit breakers in operation
Consumption
  as high as all households in Geneva area
  1/10th of the canton (11.3TWh).
2014: Preparations for Machine start-up

## Slide 8: Energy Facts & Figures
Total consumption 1 230 000 000 kWh/yr (at home ~ 11 000kWh/yr)
  43% consumed by the LHC
    Up to 14% by superconductive magnet cooling
    Up to 9% equipment cooling and tunnel ventilation
  11% by its Experiments
  30% by SPS
    7% at its Experiments
  3% PS-booster-Linac
  6% Data Centres
  7% in offices, restaurants etc.
Notes: http://cds.cern.ch/record/1324541?ln=fr Francois Duval EN/EL
61TWh consumed in Greece

## Slide 9: Water
5 million m3 of water mainly from the lake
Closed circuit of demineralised water and secondary circuit of raw water cooled in cooling towers.
Industrial process water
  Surface treatment
  Production of demineralised water

## Slide 10: Natural Gas
Heating stations at Meyrin 8 million m3
Heating station at Prevessin – 1.5million m3
Operated by external companies
  Monitor dust, CO, CO2, nitrogen oxides and sulphur oxides

## Slide 11
η ενέργεια στους επιταχυντές

## Slide 12: Accelerators at CERN
12

## Slide 13: Key Energy Consumers
Direct Energy to the beam
  RF cavities - Klystron
  Magnets
Environmental Conditioning
  Cryogenics
  Systems cooling
  Tunnel air filtering
Data
  Measurements
  Processing
Infrastructure
Other
(c) Rey.Hori / KEK

## Slide 14: Cryogenics
Cryogenic pumps are the largest single electrical consumer at CERN
Peak power: 50MW
6 weeks to cool down Helium to 1.8K to 4.2K
(c) Rey Hori / KEK

## Slide 15
The force on a charged particle is proportional to the charge, the electric field, and the cross product of the velocity vector and magnetic field:
Lorenz force:
Where q is the electrons’ (positrons’, protons’…) elementary charge:
For conservative forces (work done independent of the path) the work done by a force F along the path s1->s2 transversed by the particle is:
by differentiating:
Conclusion the magnetic field does not produce any work on the direction of the vector travelled by the charged particle. Energy (acceleration) is only gained under the effect of electric field.
Force on Charged Particle

## Slide 16: RF Cavities - Klystron
+
-
beam
Functions:
Particle acceleration
(c) Rey Hori / KEK
* The rythm of energy build up depends on the particles’ charge and the electric field voltage
Particle arrives “early”
Particle arrives “late”
Particles bunched”
t0
t1
t2

## Slide 17: Εlectro-magnets
Functions:
Beam steering
At first sight F is not dependent on mass
Since v on a circle of radius ρ-> F = centripetal force
Rearanging yields the beam rigidity i.e. a measure of the force needed to bend the charge direction
And the bending angle inside a magnet field
The integrated field is a magnet property also given by Amperes law:
*μ0: magnetic permeability of the air
* γ : lorenz factor (γ=1/(1-v2/c2)

## Slide 18: Dipole magnet
Stores energy E=0.5 L I2
Consumes power P=I2 R
(c) Rey Hori / KEK
Functions:
Beam steering

## Slide 19: Quadrupole magnets
Functions:
Focussing-defocusing
Two particles enter in the accelerator with different velocity vectors:
Particle on trajectory A (reference trajectory)
Particle on trajectory B
Betatron Oscillation

## Slide 20
1880s
the war of currents

## Slide 21: Thomas Edison VS George Westinghouse
Direct VS alternating current
AC has two key advantages
  Voltage/current can be transformed
  Current can be interrupted
Whereas DC is:
  Less dangerous* but
  May not be interrupted with standard switches
  Could not be transmitted in long distances due to the lack of dc transformers
Westinghouse won the battle!!!
  Alternating current is standard and can be transformed, transmitted to distances of several hundred kilometres and may be interrupted with standard mechanical breakers.
  It took us a century to develop technology for handling DC currents!
* If compared to a similar voltage level 50Hz alternating current of which the fluctuations can induce arrhythmia and eventually result in ventricular fibrillation of the heart

## Slide 22: Edisson VS Westinghouse
Electrical power is Ptot=voltage (v) x current (i)
Using conductors to transmit power hence Rcopper
Power is lost on the way Ploss=I2R
Hence useful power is Puseful=Ptot-Ploss
2 Solutions to save energy:
  Increase Voltage -> voltage transformation
  Decrease Resistance-> superconduction
Notice! Ploss is a function of I and R. Decreasing I by a factor of 2 decreases power loss by 4

## Slide 23: In the LHC
designed for a momentum of p=7000GeV/c per beam
Aproximately 66% of space is allowed for dipole magnets ->17617.6m
LHC circumference 26658m-> radius=4242.9m
There are 1232 main dipoles -> α=360/1232=0.29 ̊
Field in the LHC=7Tesla -> I=… for protons charged at
Notice! High current is the objective
Ploss= I2R still valid! Cannot reduce I!! But can reduce R-> superconductivity!!!

## Slide 24
Εισαγωγή στους
Μετατροπείς Ισχύος

## Slide 25: Electronics & Power Electronics
Electronics is the art of manipulating the flow of electrons to perform certain functions
  Receive, transmit and store information
  Generate electromagnetic waves (heat,light)
  Convert electricity to kinetic energy (motors
Analog &
Digital Electronics
Power Electronics

## Slide 26: Power Conversion
Electrical voltage needs to be transformed
  From direct to alternating current and the opposite
  From one voltage to another
  From one frequency to another
DC
AC
INPUT
Constant magnitude and frequency
DC
AC
OUTPUT
adjustable magnitude and frequency
rectifiers
inverters
Choppers
Cycloconverters
Notes: Similar to the mobile charger

## Slide 27: Power Converter Structure

## Slide 28: The basic power converter
Voltage regulator operation based on switching on and off the input source with a duty cycle D.
Inductor operates as averaging device

## Slide 29
Based on slide by Frederick Bordry, CERN Accelerator school 2009
Ik
Vk
ON
OFF
Ik
Vk
ON
Ik
Vk
Power Semiconductors
Transistors
Thyristors
Turn-on
Bidirectional
Low losses
Line-commutated
Self-commutated
Fast
Line-commutated
Avalache
Diodes
Power Semiconductors
Thyristors
MOSFET
IGBT
BIGTs and other
GTO
IGCT

## Slide 30: Modulation
Control of the fundamental frequency component (AC or DC) by varying the switch duty ratio

## Slide 31: Figures of merit in PE
Power conversion efficiency
  Expresses the effective-ness of a converter in converting input power to useful output power (with less wasted power in the process)
Input Power factor
  A high power factor typically indicates a lower input current for delivering a certian output power level. (as usually input sources have a stiff voltage magnitude)
Ripple factor
  Is a measure of the voltage or current ripple magnitude in dc voltage or current waveform
Total Harmonic Distortion (THD)
  is a measure of its RMS power of the harmonic components in comparison with the RMS power of the fundamental component of a voltage or current waveform.

## Slide 32: LHC – the Large Hadron collider
The beams are controlled by:
    1232 SC Main Dipole magnets to bend the beams
    392 SC Main Quadrupole magnets to focus the beams
    124 SC Quadrupole / Dipole Insertion magnets
    6340 SC Corrector magnets
    112 Warm magnets
    SC RF Cavities to accelerate and stabilize the beam
All ~8000 magnets need to be powered in a very controlled and precise manner
(in 196 circuits of ~ 6 kA)
(in 1460 circuits 60 to 600A)
(in 38 circuits 600 to 900A)

## Slide 33: Converter operating modes
+
-
1 Quadrant mode
V
V
I
+
-
+
-
2 Quadrants mode
I
+
-
+
-
4 Quadrants mode
V
I
I
V
1
2
3
4
Slide by Frederick Bordry, CERN Accelerator school 2009

## Slide 34: Current Regulation Precision
Precision components:
Current ripple
Short-term (dynamic behaviour)
Long term (reproducibility)
Typical requirements:
1-100ppm depending on application
Current in a transfer line magnet

## Slide 35: LHC Powering Challenges
Slide by Frederick Bordry, CERN Accelerator school 2009
Installation (LEP infrastructure) and Operation
  volume (a lot of converter shall be back-to-back)
  weight (difficult access) => modular approach
  reparability and rapid exchange of different parts
  radiation for [±60A,±8V] converters
  losses extraction : high efficiency (>80%) , water cooling (90% of the losses)
  high reliability (MTBF > 100’000 h)
  EMC : very close to the other equipment ; system approach

## Slide 36: LHC Power Converters
A- Elementary module [3.25 kA, 18V], [2kA,8V] :
  Switch Mode Converter (25-40 kHz, soft commutation)
  Modular approach : 4.0 kA (28) , 6.0 kA (160) , 8.0 kA (8) , 13 kA (18)
  Redundancy; small volume and weight
B- Unipolar and Bipolar converters 600A
  [± 600 A,± 10 V] : (~ 400)
  [± 600 A,± 40 V] : (~ 40)
  Energy dissipation SMPC : soft commutation ; 50-100 kHz
C- Bipolar converter [±60 A, ± 8 V] and [±120A,±10V]
  SMPC : soft commutation SMPC : soft commutation
  High reliability, radiation resistance (tunnel installation)
D- High voltage power converter [13 kA, ±180 V] (8)
  High power SCR converter and Topology studies
  Ramp (up and down) : [13 kA, ± 180 V] Flat bottom and flat top : [13 kA, 18 V]
  SCR converter : [13 kA, ± 180 V] with Active filter : ±600A,±12V

## Slide 37
+15o
-15o
3 Phase
50 Hz
Supply
Good Symmetry
Freewheel
circuit
- Used for booster of Main Bend and large warm magnets
-Voltage bandwidth < 70Hz
- Well proven
Inversion possible
Active filter (4% of the output voltage)
Two Quadrant Phase Controlled Rectifiers for high current SC magnets:
Power Converter topologies
Slide by Frederick Bordry, CERN Accelerator school 2009

## Slide 39
The load
Superconducting magnet: L= 14H
Nominal current: 20 kA
Stored energy: 2.8 GJ
Time constant: 39 hours
Time for current ramping up: 3h15m
Energy extraction system (resistor bank, not shown)
The power converter
Slide by Frederick Bordry, CERN Accelerator school 2009
20kA power converter -CMS Solenoid

## Slide 40
Subconverter
(Current source)
3.25 kA , 18V
Reactive network
+
-
n + 1 subconverters : redundancy, reliability
repairability
ease of handling underground
versatility (6.5kA, 9.75kA, 13kA, 21 kA)
13 kA, 16V
Converter
3.25 kA , 18 V
3.25 kA , 18 V
3.25 kA , 18 V
3.25 kA , 18 V
3.25 kA , 18 V
Converter modularisation

## Slide 42
The load
Superconducting magnet: L= 7.5 H
Nominal current: 20.5 kA
Stored energy: 1.6 GJ
Time constant: 37’500 s
20.5kA power converter – ATLAS solenoid
The power converter : [20.5 kA, 18V] ; (7+1) x [3.25kA,18V]
Slide by Frederick Bordry, CERN Accelerator school 2009

## Slide 43
BREAKER &
CONTACTOR
INPUT FILTER &
SOFT-START
SOFT COM. INVERTER,
50kHz..100kHz
ISOLATION &
RECTIFIER + FILTER
4Q.L.S.
Typical Converter topology (120A,10V)
Slide by Frederick Bordry, CERN Accelerator school 2009

## Slide 44
Frequency
Divider
T
1/S
yref(k)
k.Ts
ADC
Power Part
y(t)
DAC
Anti
aliasing
filter
 k
Digital
Filter
R
Ts
Over sampling
Digital controller
Tracking
Regulation
Tracking and Regulation with independent objectives
Digital control design
Slide by Frederick Bordry, CERN Accelerator school 2009

## Slide 45
Έρευνα: πιο αποδοτικά συστήματα τροφοδοσίας

## Slide 46: Compact Linear Collider (CLIC)
RF modulators are the primary electrical power consumer
Pulses of 139us 150kV and 160A resulting in bursts of 24MW per modulator
139µsec
20000µsec
Power 39GW
Notes: Klystrons (RF power generation) are the main consumer of energy
Beams of high current (relatively low energy) are created in the combiner rings
Drive beam transferred to the Power Extraction and Transfer System (PETS)
Drive beam energy is extracted through the low impedance/high impedance transformer (this is what PETS effectively is)
Drive beam is dumped
Main beam is low current but high energy (low current obviously as there is no combiner rings).

## Slide 47
Application parameters:
The load is 1638 Klystron tubes
150kV/160A 140µs flat-top required -> 24MW peak per Klystron -> 39.3GW peak load
Average power per klystron modulator 168kW
Accounting for a 90% efficiency (plug to drive beam) -> total average power 275MW
CLIC Specifications

## Slide 48
The network impedance limits the power that can be drawn.
At the rated power network impedance will be responsible for <10% voltage drop.
Drawing 39000MVA out of a 300MVA transformer would collapse the voltage (hence tripping the protections)
CLIC Grid interface

## Slide 49: From 2Q to multilevel
Q1: V: positive
I: positive
Q2: V:positive
I:negative

## Slide 50: AFE Concepts
Five level NPC
Modular-multilevel-converter (MMC)
AC Filter size |  |  | 
Control system |  |  | 
Reliability  |  |  | 
Spares inventory |  |  | 
Power range |  |  | 
Mechanical integration |  |  | 
Three phase-bridge
particularly interesting at higher voltage/power applications
Topology comparison for:
high voltage (>20kV) and
high power (>20MW) applications

## Slide 51
Ερωτήσεις;
http://www.cern.ch/aftervisit

## Slide 52: Life at CERN