## Slide 2
  ProtoDUNE cryogenics
  technical data, detailed performance and assembly time
26 October 2017

## Slide 3: Content
Experience at CERN with cryogenic systems for noble liquids
NP04 cryogenic system:
Requirements
Design Principles
Design / Fabrication
Status

## Slide 4: Experience at CERN with cryogenic systems for noble liquids (1/2)
NA48/NA62: 10 m3 of liquid krypton, continuously operating since 1996. Cryogenic system house-build.
ATLAS test area for detectors: three cryostats operated in parallel from 1997 till 2004. Cryogenic system by in house and external supplier.
ATLAS full detector tests: prototype tests station 2003 till 2005. Cryogenic system by external supplier and collaboration.
End-cap
LAr Tanks
LN2
LN2 pump
Expansion vessel
Barrel
End-Caps
LN2 phase separator
50 m3
25 m3

## Slide 5: Experience at CERN with cryogenic systems for noble liquids (2/2)
End-cap
LAr Tanks
LN2
LN2 pump
Expansion vessel
Barrel
End-Caps
LN2 phase separator
expansion vessels
12 m displacement
Liquid argon calorimeter in the ATLAS experiment:
100 m3 of liquid argon;
Operating in; underground area;
Continues in operation since 2006;
Total heat load about 12 kW;
Sub-cooled liquid argon bath;
Temperature uniformity over detector volume: < 70 mK rms;
Cooling source: evaporating LN2;
Argon purity in the ppm O2 level;
Cryogenic system by collaboration, constructed / installed by supplier.

## Slide 6
NP04 /
ProtoDUNE

## Slide 7: Design / Fabrication
CERN based cryogenics team working on the cryogenic systems of the NP01, NP02, NP03 and NP04 projects, in close collaboration with Neutrino Platform;
CERN team: 2.5 engineer; 1 technician; 2 fellow; 1 technical student;1 designer;
Contract for design, construction and installation of cryogenic system and for design and construction of cryogenic circulators are tendered via CERN;
Electrical distribution and control systems for cryogenic system are designed, produced and installed by CERN cryo-group (operational reasons)
Liquid argon contract in tendering phase
Infrastructure: Neutrino Platform

## Slide 8: Requirements for NP04 cryogenic system
Parameter | Value
LAr purity in the cryostat | 10 ms electron lifetime (100 ppt O2 equivalent)
GAr piston purge rate of rise | 1.2 m/hr
TPC cool-down rate | < 40 K/h, but vertical gradient <10 K/m
Nominal LAr purification flow rate | 5.5 days / volume change (4m3/hr)
All surfaces in the ullage during operation | < 100 K
GN2 purge within insulation | 1 volume change/day
Cooling power | 2.4 kW static cryostat 2.6 kW cryo system and electronics

## Slide 9: Design Principles
720 ton LAr
1: Gas piston purge system before cool-down;
1
2
2: Cool-down system, creating mixture liquid and gaseous argon, dispersed by second gas flow
System also partially based on ICARUS experience.
4: Liquid argon is taken by pump and circulated through liquid purifier, condenser, phase separator
3: Gaseous argon from feed through towers is constantly circulated through purifier and re-liquefied

## Slide 10: Design Principles
2: Circulation through liquid purifier during normal operation
Active Cu based purification system
1: Circulation through liquid purifier during liquid filling
3: Circulation through gaseous purifier during gaseous purges
4: Circulation through gaseous purifier during normal operation
Experience WA105: O2 equivalent impurities after 7 liquid volume passages: < 30 ppt

## Slide 11: Purification principle
Oxidation – 87K
Regeneration – 420K
Cu-226 ( Cu coated Al2O3 )
Activation
“Controlled reduction of atmosphere exposed Cu-226”
“very” exothermal, 0.5 % hydrogen
Regeneration
“Controlled reduction of Cu-226 oxidised in purity conditions”
exothermal, 2.5% hydrogen
Molecular Sieve
Moisture adsorption

## Slide 12: Time line
* After approval of functional proposal
Conceptual design (CERN): 3 months*
Contract supplier
(4 months)
Engineering by supplier
3 months
Order long lead items
(3 months)
Fabrication
3 months
Order very long lead items (CERN):
9 months
Installation 6 weeks
Little over one year

## Slide 13: Present status
Cryogenic platforms ProtoDUNE
Cryo control racks

## Slide 14: Cryogenic system in near future inside
Delivery cryogenic hardware from beginning of 02/2018

## Slide 15: Cryogenic system in near future inside
9.5m
WALKWAY
emergency door
EHN1 EXTERNAL CRYOGENICS
ELEMENTS
Cryo Tank 50[m3]
H2 Bottle Rack
Mech Filter Cryo
Ar Vaporizer
Field Boxes
Warm Panel
LAr cryolines
LN2 cryolines
Warm lines
Cryo Tank 11[m3]
Mixer
Purifier regeneration station
7m
LN2
LAr
LAr