## Slide 1: M. Battistin (EN/CV/DC) 1st September 2009
ATLAS cooling Group - Thermosiphon solution for ATLAS ID cooling

## Slide 2: HAUG compressors show technical limits
PR
thermal
screen
others
4 liquid lines
4 gas lines
6 Haug
compressors
condenser
liquid
tank
pneumatic
valve
manual
valve
manual
valve
dummy
load
mixed water
Sub-cooler
BPR
pixel
6 X SCT
manual
valve
pneumatic
valve
ATLAS requested to evaluate a possible alternative to the present compressor station. The main reasons are:
Reliability: many failures registered in the present compressors
Cleanliness: wear of components obliges to an important filtering process
Leaks: developing with time due (in part) to vibrations
UX15
USA15

## Slide 3: A thermosiphon solution
PR
thermal
screen
others
4 liquid lines
4 gas lines
condenser
liquid
tank
pneumatic
valve
manual
valve
manual
valve
dummy
load
Heater
BPR
pixel
6 X SCT
manual
valve
pneumatic
valve
A gravity driven circulation (thermosiphon) could be a solution.
The thermo-siphon solution could provide:
Reliability: no active component in the system
Cleanliness: no wear of components
Leaks: reduction of connection points and no vibrations
Low temperature
Chiller
UX15
USA15
USA15
Surface

## Slide 4: A low efficiency cycle
A
B
C
D
E
F
E1

## Slide 5: P&I of the installation
-55 °C = 400 mbar
-67 °C = 200 mbar
-40 °C = 850 mbar
-30 °C = 1300 mbar
-25 °C = 1670 mbar
Return DP = 80 mbar
2 kW
6 kW

## Slide 6: The project organization
Alexandre Moraux, Elena Perez, Michele Battistin, Jose Direito, Jan Godlewski, Lukasz Zwalinski, Danilo Giugni, Antonio Romanazzi, Johan Bremer.
Thermo-siphon first action list:
First Workshop on thermo-siphon solutions at CERN 6th July 09.
First internal review at CERN 1st September 2009.
Technical and economical definition of the low temperature chiller solution – Visit to first possible supplier on June 29th.
Provisional design of the first prototype – August 09.
Presentation of the technical solution to ATLAS ID end of Sept 09.
Installation of the transfer lines in the PX15 – September 09.
Prototype assembly – Oct-Dec 09.
Commissioning and test – Jan - March 10
There is a need/possibility of a fast and intermediate prototype to be installed with recuperation material using an high of ≈15 meters in bdg 191.

## Slide 7: Conclusions
Gravity driven circulation evaporative cooling systems seems a promising technology to replace the compressors in the evaporative cooling systems
It is foreseen to install a test bench in PX15; the design parameters of this test bench installation fit with ATLAS IBL cooling needs.
We are evaluating the need to realize a very small scale test bench to validate the first design assumptions in bdg 191
Perfluorocarbon blends solutions could be adopted to the thermo-siphon to improve the performances. Azeotropicity could be a problem.