## Slide 1: 11T Trim Power Converter Connection to Leads
Samer Yammine
TE-EPC Technical Discussion – 2017-11-01

## Slide 2: Background
A demand from WP6a to connect the 11T trim PC to 2 leads/polarity
Rationale: To use the LHC conduction cooled 120 A leads
11T Trim Current Profile for 7 TeV Operation
LHC Conduction Cooled Leads
Current Lead Integration
Flange

## Slide 3: Requirements
Ensure Protection of leads (voltage threshold): 4 vs 2 in LHC
Ensure current equilibrium in operation
Ensure that the current does not surpass 125 A per lead
If not, discharge the trim circuit under 10s
11T Trim Current Profile for 7 TeV Operation
LHC Conduction Cooled Leads
Current Lead Integration
Flange

## Slide 4: Solution Proposal
2x70mm2 DC cables per polarity for current equilibrium during operation.
New radiation-tolerant card + 4 current sensors (1 per DC cable) to generate a slow power abort signal to the PC in case of ΔI > 5A or I > 125A.
Extension of already existing card that monitors the CLs voltage from 2 inputs to 4.

## Slide 5: Slow Power Abort
The 11T power converter is in parallel to a cold diode
dI/dt < 5V/0.132H – 20 % margin < 30 A/s
SPA of 11T: ramp from - 250 A to 0 A with 30 A/s  8.33 s

## Slide 6: Thanks for your attention