## Slide 1
Claudio Bortolin EP-ADO-PO
ACES 2018, April 26, 2018
Counting rooms constraints and cooling studies

## Slide 2
2,5 MW  2,7 MW
440 m3/h
26 – 31,3 °C
1,46 MW
350 m3/h
12,2 – 15,8 °C
350 kW
100 m3/h
12,5 – 15,5 °C
673 kW
5 – 11°C
95 m3/h
28 kW
5 – 5,7 °C
35 m3/h
430 kW
4,6 – 6,6 °C
185 m3/h
1,4 MW
5 – 11 °C
200 m3/h
1,4  2,5 MW
537 m3/h
30 – 34 °C
1100 kW
330 m3/h
12,5 – 15,5 °C
5,7 MW
24 – 29 °C
980 m3/h
100 m3/h
Detector cooling
HVAC in USA15, SR
HVAC surface
HVAC surface
(ex SU1)
HVAC for
ATLAS caverns
Detector cooling
Racks USA15
Racks SDX1
2,5 MW
386 m3/h
5 – 10,6 °C
Redundancy
Cooling capacity available… in ΔT only
To be verified what is the contribution of the actual racks heat losses on the HVAC
Mixed water flow is at nominal conditions
Redundancy
Situation in 2016

## Slide 3
Muons 60 kW
ΔT =4K
12.5 m3/h
Yoke 60 kW
ΔT =2K
25 m3/h
BusBar 140kW
ΔT =9.5K
13 m3/h
Ecal 420kW
ΔT =1.6K
226m3/h
Racks 2620kW
ΔT =6K
376m3/h
Design values:
Cooling capacity available… in ΔT
Racks 544kW
ΔT =1.2K
390m3/h
Real value
Mixed water flow is at nominal conditions
Situation in 2016

## Slide 4
To compare different configurations (horizontal and vertical airflow) identifying any boundary condition
We needed to study the impact of the ATCA integration in the USA15 counting rooms
To evaluate the impact on the safety of the environment (i.e.: noise)
Racks cooling evaluation: Why?
To assess the efficiency of the existing cooling infrastructures: cooling power available only in ΔT. Impact of the heat losses on the HVAC.

## Slide 5: Test campaign 2016/17: Inside the shelves
Zone 1
Zone 2
Zone 3
Zone 4
Inlet 1
Inlet 2
Rear
Front
Comtel load blades: maximum power 350W
Front
Rear
ASIS load blades: maximum power 600W
14 x Comtel blades: 6* Embedded Temperature sensors (green) + 6 air T sensors (blue)
14 x ASIS blades: 6 Temperature sensors (inlet and outlet)
3x
1x
3 x 3 fans on the top, 1 x 6 fans on the bottom. 96 W x fan (nominal). Power measured was 140W/fan.

## Slide 6: (ATCA2 14x450W, ATCA1 14x350W, water flow 3m3/h)
C
o
o
l
I
n
g
D
o
o
r
Air Inlet
Air Outlet
Air Inlet
Schroff 14U with Comtel LB
ASIS 16U with ASIS LB
Air Outlet
23.8°C
23.2°C
21.9°C
21.7°C
21.5°C
34.4°C
32.7°C
31.7°C
31.7°C
20.8°C
22.1°C
∆T=3.1°C
Q= mCp (Tout- Tin) = 0.83 × 4.18 ×3.1=
= 10.8 kW (78% of the total power)
Water inlet temperature 14.6°C ±0.3°C
Total power 13.9kW
Horizontal cooling: equipment and sensors layout
3 kW released to the environment in forced convection-> HVAC in USA15 already at the maximum.

## Slide 7
Av. ∆T = WBF-BF = 3.6K
ASIS Crate 14x450W
ASIS Crate 14x350W
Schroff Crate 14x350W
Av. ∆T = WBF-BF = 1.5K
Av. ∆T = WBF-BF = 1.4K
ASIS crate performance with bottom fans working is better than with only top fans (the average maximum temperature of the blades is 3.6K lower, while power dissipation is 450W per blade);
Schroff crate performance is poor in both cases although with only top fans working the airflow is much more homogeneous.
Average max T | 
WBF [°C] | BF [°C]
50.4 | 46.8
Average max T | 
WBF [°C] | BF [°C]
53.6 | 52.1
Average max T | 
WBF [°C] | BF[°C]
42.9 | 41.5
Comparison between tests with and without bottom fans
Water inlet temperature 14.6°C ±0.3°C
WBF – without bottom fans
BF – with bottom fans

## Slide 8
Water flow 3m3/h |  | Water flow 2.4m3/h |  | Water flow 1.8m3/h (same as ATLAS CR) | 
ASIS top | ASIS bot | ASIS top | ASIS bot | ASIS top | ASIS bot
23.8°C | 22.4°C | 24.4°C | 23.4°C | 25.1°C | 24°C
23.2°C | 23.8°C | 23.9°C | 24.8°C | 24.5°C | 25.4°C
21.9°C | 21°C | 22.6°C | 21.9°C | 22.1°C | 22.2°C
21.7°C | 20.6°C | 22.3°C | 21.6°C | 21.8°C | 22°C
21.5°C | 20.7°C | 22.1°C | 21.4°C | 22.6°C | 21.7°C
22.4°C | 21.7°C | 23.1°C | 22.6°C | 23.2°C | 23.1°C
Cooling Door
ASIS crate 14x450W
Schroff crate 14x350W
The lower the water flow, the higher temperature of the air released to the environment.
Placing the crate which produce more heat on the bottom of the rack causes more efficient distribution of the heat through the rack and decreases the temperature of the released air to the room.
Av. outlet T
Water inlet temperature 14.6°C ±0.3°C
Repositioning of the crates (air outlet temperatures)

## Slide 9: Vertical cooling configuration
30 T sensors were installed. Their layout was changed according to the kind of tests we were carrying out.
Plexiglas panel
Heat exchange area
Air/water heat exchangers (1U), providing up to 3.8 kW of thermal capacity each
Back view of the heat exchanger
Exchanged surface reduced (overlapping only 56%)
Plexiglas panel installed to improve the leak tightness
Heat exchangers T sensors
Flow stopper
2U
Turbines– 4U
Heat exchanger -1U
ATCA 2 – 14U
ATCA 1 – 14U
2 Heat exchangers – 2U
Heat exchanger – 1U
Air Deflector – 2U
Power supply 2 – 3U
Power supply 1 – 3U
52U
B. 4 Tdaq Lab

## Slide 10
Vertical cooling performance (without bottom fans)
Average max T | 
Top [°C] | Bot [°C]
50.4 | 49.2
Average max T | 
Top [°C] | Bot [°C]
51.25 | 49.1
Average max T | 
Top [°C] | Bot [°C]
51.25 | 49.2
Average max T | 
Top [°C] | Bot [°C]
50.4 | 49.1
Boards average temperatures are matching the max target T (50°C)

## Slide 11
Configuration (in both cases only top fans were working on maximum speed):
Vertical: Top – 14x450W Comtel LB in ASIS crate, Bottom – 14x450W ASIS LB in ASIS crate. Water temperature 13°C.
Horizontal: Top – 14x350W Comtel LB in Schroff crate, Bottom – 14x450W ASIS LB in ASIS crate. Water flow 2.4m3/h, water temperature 13°C.
Vertical - Horizontal cooling comparison in b4
Average max T | 
Vertical [°C] | Horizontal [°C]
49.2 | 48.75
The cooling performance are very similar.

## Slide 12
Total power 13.9kW
Comparison of heat removal for different water temperatures
T° / Hygrométrie à la reprise | Régime d'eau ( °C ) | Puissance ( kW ) | Débit d'eau ( m3/h ) | T° / Hygrométrie au soufflage | Perte de charge batterie ( mCE )
33°C / 10 g/Kg air sec | 13 / 18 | 14 | 2.4 | 22.5°C / 10 g/Kg air sec | 2.13
33°C / 10 g/Kg air sec | 14 / 19 | 13 | 2.24 | 23.2°C / 10 g/Kg air sec | 1.87
37°C / 10 g/Kg air sec | 13 / 18 | 18 | 3.09 | 23.5°C / 10 g/Kg air sec | 3.39
37°C / 10 g/Kg air sec | 14 / 19 | 17 | 2.93 | 24.2°C / 10 g/Kg air sec | 3.06
Cooling door specifications
Many better products are available in the market

## Slide 13
ATCA 63U rack: SR1 new test setup
Hardware
3x Vertically cooled ATCA shelves
3x 14 Load Blades
Target power capacity to test is 450W/blade=18.9 kW
New dedicated chiller with 25 kW cooling capacity
“TwiceMe” rack
prototype in SR1
  Main goals for the 2018 test cooling campaign:
  Assessing the cooling capabilities with 3 ATCA shelves
  Investigating efficiency of the new 2U heat exchangers: 7.7 kW cooling capacity, dimensions optimized for ATCA shelves
  Checking cross-shelf dependency in new layout – failure modes tests
  Noise assessment with 3 shelves and installing soundproofing material
  Investigating the influence of side gaps soundproofing material on the rack cooling performance
  Checking the different fans configuration influence on the cooling performance of new ATCA crates
  Ready to test new 14U vertical cooling Schroff shelves selected as standard at CERN
New 2U heat exchanger concept
Turbine– 4U
ATCA 3 – 14U
ATCA 1 – 14U
Air Deflector – 2U
1 Heat exchanger -2U
ATCA 2 – 14U
1 Heat exchanger -2U
Power supply 1 – 3U
Power supply 2 – 3U
free–3U
1 Heat exchanger -2U

## Slide 14
Pentair/Schroff ATCA shelves
  14 ATCA slots w. RTM
  Vertical or Horizontal cooling
  DS or FM topology
  40 or 100G backplane
  Bussed IPMB
  1 Shelf man. included
-48Vdc rectifier system (UniPower)
  14 kW max output pwr
  11 kW with N+1 redund.
  Based on 5 pwr bricks
  Up to 12 CB output
  Ctrl module (SNMP over eth.)
ATCA shelf and - 48V PSU procurement
The first prototype of the selected Schroff shelf is being installed in our 63U rack for tests
14
Prices available upon request

## Slide 15
ATCA 63U rack installed in the laser room
Dedicated Chiller with 25kW cooling capacity installed outside the room
Water piping are insulated for cold water tests
New Schroff shelf
Comtel new load blades maximum power 800W
6x HXs (1U)

## Slide 16: Cooling tests results (without bottom fans)
The test was carried out in following configuration
  ATCA 3 (top crate) – 14xComtel LB (old type), top fan trays working on maximum speed
  ATCA 2 (middle crate) – 14xComtel LB (new type), top fan trays working on maximum speed
  ATCA 1 (bottom crate) – 14xASIS LB, top fan trays working on maximum speed
Chart: 14x350W Comtel LB (top) 14x400W Comtel LB (mid) 14x400W ASIS LB (bot)
| s13 | s11 | s9 | s7 | s5 | s3 | s1 | s2 | s4 | s6 | s8 | s10 | s12 | s14
Top shelf | 59 | 54 | 53 | 52 | 53 | 54 | 51 | 51 | 51 | 52 | 52 | 51 | 50 | 54
Bottom shelf | 56.25 | 57.5 | 53.75 | 55 | 57.5 | 52.5 | 53.75 | 52.5 | 51.25 | 52.5 | 51.25 | 52.5 | 52.5 | 53.75
50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
Average max T | 
Top [°C] | Bot [°C]
52.64 | 53.75
With the inlet temperature of water at 15C, the average maximum temperature on the blades is slightly above 50C. Circuit breaker tripped when we tried to reach 450W.
63U results!
Preliminary
Water inlet T 15°C
Flow 4.5m3/h

## Slide 17: Comparison between tests with and without bottom fans
The test was carried out in following configuration
  ATCA 3 (top crate) – 14x350W on Comtel LB (old type)
  ATCA 2 (middle crate) – 14x350W on Comtel LB (new type)
  ATCA 1 (bottom crate) – 14x350W on ASIS LB
On the less air resistive blades (Comtel – old type), it can be seen that the airflow is much less homogeneous and the overall average max T is higher by 2.5K when the bottom fans are in use.
In case of LB with high air resistance (ASIS) we can see that the cooling performance is better when the bottom fans are used.
Water inlet T 15°C
Flow 4.5m3/h
Chart: 14x350W Comtel LB.
| s13 | s11 | s9 | s7 | s5 | s3 | s1 | s2 | s4 | s6 | s8 | s10 | s12 | s14
WBF | 58 | 53 | 52 | 51 | 52 | 53 | 51 | 50 | 50 | 51 | 51 | 51 | 50 | 54
BF | 60 | 60 | 53 | 51 | 55 | 59 | 54 | 55 | 49 | 51 | 54 | 59 | 52 | 50
50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
Average max T | 
WBF [°C] | BF [°C]
51.93 | 54.43
Chart: 14x350W ASIS LB.
| s13 | s11 | s9 | s7 | s5 | s3 | s1 | s2 | s4 | s6 | s8 | s10 | s12 | s14
WBF | 52.5 | 53.75 | 50 | 51.25 | 53.75 | 50 | 50 | 48.75 | 48.75 | 48.75 | 48.75 | 48.75 | 48.75 | 50
BF | 46.25 | 50 | 46.25 | 45 | 47.5 | 46.25 | 48.75 | 46.25 | 43.75 | 46.25 | 45 | 47.5 | 45 | 45
50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
Average max T | 
WBF [°C] | BF [°C]
50.27 | 46.34
WBF – without bottom fans
BF – with bottom fans
63U results!
Preliminary

## Slide 18
ATCA 63U rack first issues and limitations
The mechanical structure of the rack must be improved, shape of the front access is not rectangular. Cable trays are not sufficient to hold the door weight. Supplier being informed.
Nominal shape
Real shape (but not so dramatic)
The external panels are quite thin (to save weight?), they vibrate easily and they become an additional source of noise. With soundproofing the effect is anyway reduced.
- Shelves fans dissipate 6.1kW (≈150W/fan) at the maximum speed
User power = 42 boards at 375W (average power) = 15.75 kW
2 PS (Power-One GND.S.48.M27) can provide up to 14.5kW/each (with 5 rectifiers).
Circuit breakers are not well power balanced because of different power demand of each socket of the shelves…we need time to solve the problem.
Chiller water outlet temperature still oscillating too much. PID to be tuned.
User max power available per rack with 400W/board is 16.8kW

## Slide 19
 | 1 | 2 | 3
Doors open | 97.2 | 92.7 | 92.4
Doors closed | 85 | 83.1 | 92.4
Delta dBA | 12.2 | 9.6 | 0
 | 1 | 2 | 3
Doors open | 99.4 | 96.4 | 94.2
Doors closed | 86.9 | 85.7 | 94.2
Delta dBA | 12.5 | 10.7 | 0
 | 1 | 2 | 3
Doors open | 97.2 | 92.7 | 92.4
Doors closed | 87.8 | 84.1 | 92.4
Delta dBA | 9.4 | 8.6 | 0
All values in dBA
Fig.1. Test with only top fans working at maximum speed.
Fig.2. Test with top and bottom fans maximum speed.
Noise suppression material: Acoustic foam
Noise reduction: measurements (horizontal shelves)
Noise suppression material: Masse lourde
 | 1 | 2 | 3
Doors open | 99.4 | 97.4 | 94.3
Doors closed | 90.1 | 87.8 | 94.3
Delta dBA | 9.3 | 9.6 | 0
New sound suppression material: Masse lourde
Discussion with an external company is on-going in order to upgrade the counting rooms including a sound proof area for the ATCA racks and active noise reducers.
Side gaps insulated (air gaps reduction in vertical) with panels and rear door to check the noise reduction and how it affects the cooling efficiency.
Fig.2. Test with top and bottom fans maximum speed.
Fig.1. Test with only top fans working at maximum speed.
Masse lourde

## Slide 20
Chart: 14x350W Comtel LB (top) 14x450W ASIS LB (bot)
| s13 | s11 | s9 | s7 | s5 | s3 | s1 | s2 | s4 | s6 | s8 | s10 | s12 | s14
Without soundproofing | 51.5 | 50 | 47.75 | 50 | 52.25 | 48.75 | 50 | 48.75 | 48.75 | 48.75 | 47.75 | 47.75 | 48.5 | 48.5
With soundproofing | 53.75 | 51.25 | 52.5 | 52.5 | 52.5 | 50 | 48.75 | 50 | 51.25 | 52.5 | 50 | 52.5 | 52.5 | 55
50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
Here below you can see the comparison between the cooling performance of the rack equipped with soundproofing material and the rack without soundproofing material:
ASIS load blades
Average max T | 
WOS [°C] | WS [°C]
49.2 | 51.8
WS – With Soundproofing
WOS – Without Soundproofing
Chart: 14x350W Comtel LB (top) 14x450W ASIS LB (bot)
| s13 | s11 | s9 | s7 | s5 | s3 | s1 | s2 | s4 | s6 | s8 | s10 | s12 | s14
Without soundproofing | 56 | 54 | 53 | 52 | 53 | 54 | 51 | 53 | 54 | 53 | 52 | 53 | 52 | 53
With soundproofing | 51 | 48 | 49 | 49 | 49 | 50 | 49 | 49 | 49 | 49 | 50 | 51 | 49 | 49
50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
Comtel load blades
Average max T | 
WOS [°C] | WS [°C]
53.1 | 49.4
Comtel load blades average maximum temperature difference is 3.7K in favour of soundproofed rack while ASIS load blades the temperature difference is 2.6K in favour of not soundproofed rack.
Soundproofing: Influence of the soundproofing material on the T distribution
Vertical

## Slide 21
 | Water flow 3m3/h |  | Water flow 1.8m3/h (same as in USA15) | 
 | 52U (4HX) | 63U (6HX) | 52U (4HX) | 63U (6HX)
∆T of the water | 3.2°C | 5.0°C | 4.9°C | 8.4°C
Power removed | 11.15kW | 17.42kW | 10.28kW | 17.56kW
% of the total power | 79% | 85% | 73% | 85.5%
52U total power 13.9kW
63U total power 20.5kW
Heat removal with soundproofing: 52U vs 63U
In May 2018 we will start testing with new 2U Heat exchanger…let’s see if we can do better.

## Slide 22
Noise on Vertical cooling: doors and side air gaps insulated (52U)
1
2
2
rack
Noise measurement points
Vertical air flow
A reduction of 3 dB(A) is quite significant considering the total number of racks will be operative in the counting room (>50)
63U noise measurements coming soon….
Noise measurements (52U) | Pos. 1 Door open [dB(A)] | Pos. 1 Door closed [dB(A)] | Pos. 2 [dB(A)] | Av. max T on ASIS LB [°C] | Av. max T on Comtel LB [°C]
Without insulation | 102.8 | 90 | 87.5 | 49.2 | 53.1
With insulation |  | 86.3 | 84 | 51.8 | 49.4
Difference |  | -3.7 | -3.5 | 2.6 | -3.7

## Slide 23
The mixed water used in the counting rooms for both, ATLAS and CMS, are working at lower performance than the design one.
While the the mixed water flow is nominal the ΔT is significantly lower than the design. Cooling capacity available in ΔT is 50% for ATLAS and 80% for CMS.
ATCA tests: In both configurations, horizontal and vertical, the load boards temperature at the maximum power is very close and sometime above to 50C: the tests were carried out with an average power on the rack of 400W/board
The cooling capacity in vertical and horizontal configurations is very similar (about 80%), at lower water flow the vertical solution is slightly more efficient
Equipping the rack with soundproofed materials does not affect in a significant way the temperatures distribution, it increases the cooling efficiency reducing the thermal losses through the rack walls and it lowers the noise in a significant way
A new 63U ATCA rack is operative in SR1, new 2U heat exchangers will be delivered soon
  Water chiller must be tuned, power distribution to the circuit breakers must be equalized.
  New 2U heat exchangers prototype were delivered today. Common interest/effort of ATLAS and CMS.
Conclusions