## Slide 1: Development of a Cryogenic System for the FCC-hh Inner Triplets Cold Mass Cooling
Dimitri Delikaris, Claudio Kotnig, Laurent Tavian

## Slide 2: FCC Inner Triplets – Structure & Heat Source
The FCC-hh Inner Triplets
Final focussing magnets before Interaction Points (8 quadrupoles in 3 groups)
0.655 m
Collision debris

## Slide 3: FCC Inner Triplets – Heat Load on Tungsten Shield
- Tungsten Shield cooling between 40 – 60 K (compared to 1.8 K of Cold Mass)
- Large cooling channels in tungsten shield possible (due to impact distribution)
Heat Load on the Tungsten Shield
Due to high specific heat load original Q1B magnet (“Q1Borig”) was split
Rapid Reaction Team
Besana MI, Cerutti F, Delikaris D, Humann B, Martin R, Schörling D, Tavian L

## Slide 4: FCC Inner Triplets – Cold Mass Cryogenics
Heat Load on the Cold Mass
Stainless Steel Collar
Iron Yoke
dmax ≈ 100 mm
Available space for cryogenics installations
Tmax = 1.9 K
Free space for pressurized su-perfluid helium
Coil
Tmax = 4.5 K
Two approved cooling concepts with superfluid He:
Two-phase cooling with bayonet heat exchanger pipe
(Pure) Conduction cooling
Available space for cryogenics installations is limited
Available driving temperature range for heat extraction is limited
The range of specific heat loads varies strongly for the single magnets
→ Small, reliable and possibly uniformly designed cryogenic system needed

## Slide 5: FCC Inner Triplets – Two-phase cooling
The two-phase cooling scheme
Feeder Pipe
Level Gauge
  Cold mass immersed in a pressurized static bath of superfluid helium
  Header C
  Header B
TC = 4.6 K
pC = 3 bar
Helium supplied by header C:
pB = 16 mbar
Helium discharged into header B:
→ Determines stratified flow temperature
(= T )
pSat=17 mbar

## Slide 6: Two-phase cooling - The two main constraints
Heat extraction
Bad heat transfer via vapour phase
Good heat transfer via liquid phase
Relative movement between liquid and vapour phase determines shape of the surface:
Vapour velocity
Increasing vapour phase velocity
vVap
vLiq
vVap
vLiq
vVap
vLiq
DTmax
Pwet
hLL
AVap
Tmax = 1.9 K
T2F ≈ 1.81 K
Maximal vVap determined in experimental setup
Minimal hLL for sufficient heat transfer

## Slide 7: Two-phase cooling – Analytical estimations
Analytical estimation
  Intersection point with helium 5 m/s-isotach yields minimal diameter
  → for Q2C the minimal inner diameter is about 70 mm

## Slide 8: Two-phase cooling – Mathematical Model
Steady-State Calculation
  Mass balance:
  Momentum balance:
  Thermal energy balance:
  Thermal conduction in superfluid helium:
  Longitudinal pressure drop in the two phases equal
  Solving for minimal HX pipe diameter
  Smooth stratified flow regime in HX pipe
  Conditions:
  Modelling 1D-equations:

## Slide 9: Two-phase cooling – Numerical results
Numerical solutions
  Fullfilling backflow mass conservation
  Solid permanent liquid helium sump
  No permanent liquid helium sump
  Comparisons with former experimental results indicate an over-estimation of the wave generation of the model (vVap < 5m/s)
  → The requested maximal diameter of 100 mm seems to be feasible

## Slide 10: FCC Inner Triplets – Conduction Cooling
The conduction scheme
  Needed cross section area for heat conduction α L1.3
  → Conduction cooling is advantegeous for short magnets (like in the Inner Triplets)
  Option 1: One-Side-Cooling
  Option 2: Two-Sides-Cooling
  Two possible designs:

## Slide 11: Conduction cooling – Numerical results
Numerical solutions
The Two-Side Conduction cooling option and the Two-Phase cooling need similar space in the cold mass for cryogenics - both concepts seem to be in the feasibility’s range
The choice could be made by different aspects (required space between adjacent magnets, transient behavior, controlling effort, reliability, …)

## Slide 12: Summary & Outlook
Summary
Very high, but strongly non-uniform heat loads on the FCC Inner Triplet Magnets challenge the cryogenics design (structure was changed to be able to design a reliable cooling system for the available space)
Two well-established cooling concepts were investigated
Less space needed for cryogenics
Robust concept and simple controlling
Two-Phase Flow Cooling
Pure Conduction Cooling
With both cooling concepts the space requirements are in the range of feasibility – the possibility of choosing between different designs provides freedom of choice for taking into account other aspects as well

## Slide 13: The end
"What starts out as science fiction today may wind up being finished tomorrow as a report.“
Norman Mailer
Thank you very much for your attention!

## Slide 14: Supplemental – Wall Shear Stress (Liquid)
α tLiq-Wall
Wall Shear Stress

## Slide 15: Supplemental – Two-Sides vapour extraction
Two-Sides vapour extraction
  Two-Sides vapour extraction could decrease bayonet HX diameter size requirement

## Slide 16: Supplemental – Conduction Cooling Interconnections
Conduction Cooling Arrangements
  Two-Sides-Cooling
  One-Side-Cooling
  General HX for Two-Sides Cooling to assure balancing
  Combined helium baths for adjacent magnets
  One Jumper connection (HX, valve) for two adjacent magnets for One-Side Cooling

## Slide 17: Supplemental – Conduction Cooling Vapour Generation (1/2)
  rLiq = 145 kg/m3
  HX pipe diameters calculated to reach a temperature of ≈ 1.9 K
  Minimal pressure head needed to avoid saturation line (≈ 42 cm)
Conduction Cooling Vapour Generation (1/2)

## Slide 18: Supplemental – Conduction Cooling Vapour Generation (2/2)
  Liquid helium temperature in HX pipe < 1.9 K for radial heat transfer
  Two parallel longitudinal heat fluxes (in HX pipe and static helium bath)
  Radial driving temperature difference increases towards outlet
  Limit determined by the magnets Q1A and Q3B (T = 1.887 K → 30 – 40 cm head)
Conduction Cooling Vapour Generation (2/2)

## Slide 19: Supplemental–Mixed Cooling Concepts
Mixed Cooling
High-loaded magnets: Two-Sides Conduction Cooling
High-loaded magnets: Two-Sides Conduction Cooling
Low-loaded magnets: Combined bayonet heat exchanger cooling