## Slide 1: Infrastructures and Operation Summary
Johannes Gutleber
Accelerator and Technology Sector Directorate Office, CERN, Switzerland June 25, 2019
Overview
Wednesday-Thursday
Cryogenics
Safety
Technical infrastructure
Implementation aspects
Summary

## Slide 2: Cryogenics

## Slide 3
Process cycle options
Helium
compressors
He-Ne-mix compressors
Qbs+Qts 40 to 60K
Qcl
40 to 290K
Qcm 1.9K
T1
T2
T3
T4
T5
T6
CC1
CC2
CC3
CC4
CC5
HX1
HX2
HX3
HX5
HX6
HX7
HX8
HX4
HX9
tunnel
cavern
Ground level
shaft
Concept A – Ne/He precooling
FCC-hh CDR proposal
Helium
compressors
T1
T2
T3
T4
CC1
CC2
CC3
CC4
CC5
HX1
HX2
HX3
HX5
HX6
HX7
HX8
HX4
HX9
tunnel
cavern
Ground level
shaft
T5
T6
Concept B – Pure Helium
LHC-like option
Qbs+Qts 40 to 60K
Qcl
40 to 290K
Qcm 1.9K
Helium
compressors
Nitrogen compressors
T1
T2
T3
T4
T5
T6
CC1
CC2
CC3
CC4
CC5
HX1
HX2
HX3
HX5
HX6
HX7
HX8
HX4
HX9
tunnel
cavern
Ground level
shaft
Concept C – LN2 precooling
ITER-like option
Qbs+Qts 40 to 60K
Qcl
40 to 290K
Qcm 1.9K
Evaluation of three precooling options down to 40K
Estimation of performances and pre-design of components
F. Millet (CEA)
Industry studies for FCC-hh Cryoplants

## Slide 4
F. Millet (CEA)
Conclusions
Notes: conclusions of the Linde and Air Liquide studies are :
- no showstopper identified by industries for the 100kW @ 4.5K plants
- more energy-efficient cryoplants feasible with additional R&D actions on large-scale rotating machines (warm and cold compressors, energy recovery)

## Slide 5: Nelium Turbo-Brayton cycle improvement
Problem statement:
Nelium mixture composition improvement is limited with centrifugal compressor design.
1-tandem machine is available for 40 vol. % of helium.
Baseline cycle
Image courtesy: MAN Diesel and Turbo
S. Savelyeva (TUDresden)

## Slide 6
New cycles baseline was offered to improve the system components design
 2 inner heat exchangers |  reduced pressure ratio |  reduced pressure ratio
 |  easier pressure control |  higher volumetric flow to the second compressor casing
 |  |  reduced pressure ratio of pre-cooling turbine compared to cycle B
 higher pressure ratio |  additional heat exchanger |  additional heat exchanger
 |  high speed of the pre-cooling turbine (high pressure ratio) | 
Nelium Turbo-Brayton cycle improvement
Improved baseline
Cycle A (baseline)
Cycle B
Cycle C
Helium content can be increased up to 60 vol. % He to reduce heat exchangers sizes
- Remove 1 compressor impeller → +4..5 % to the total compressor efficiency ηs↑
or
Main future target: adjust the Turbo-Brayton cycle design to help the industrial turbo-compressor design
S. Savelyeva (TUDresden)

## Slide 7: FCC Inner Triplets Cooling – Heat Source
Cryogenics’ task is to extract heat load generated by collision debris in the IP
Collision debris
High and strongly varying specific heat loads call for large cryogenics installations or very short cooled units
C. Kotnig (CERN)

## Slide 8: FCC Inner Triplets Cooling – Cooling Schemes
Two-Phase Flow Cooling
Pure Conduction Cooling
Two cooling concepts based on superfluid helium technology were investigated
Both systems could fulfil the cooling task with the available space in the cold mass for the current Inner Triplet design
Small increases of magnetic lengths (e.g. for optical reasons) are within the margins and favors the application of the two-phase cooling concept
Less space +
more flexible for different lengths
Better suited for short magnets
C. Kotnig (CERN)

## Slide 9
Johannes Gutleber
Accelerator and Technology Sector Directorate Office, CERN, Switzerland June 25, 2019
Development of a heat transfer model compared to experimental data.
Steady state model looks OK
Transient under development
A. Vitrano (CEA)

## Slide 10: He II Model Validation
Research question
Experime-ntal setup
Numerical model
Ongoing work
Heat Flux ≈ 22 [kW/m2]
Tbath = 1.8102 [K]
Also a simplified model looks promising in terms of qualitatively forecasting the heat transfer behavior. Work ongoing to validate and consolidate the model.
A. Vitrano (CEA)

## Slide 11: Technical Infrastructures and Safety

## Slide 12
Identification of hazards, based on project breakdown structure, and “Standard Best Practice” to cope with them.
Three safety domains require special treatment:
  Fire in underground facilities
  Cryogenics in underground facilities
  Radiation Protection
Safety performance based study for Fire and Cryogenics
Standard prescriptive measures for Radiation Protection
Scope of the CDR Safety Study
Future Circular Collider Study
FCC Week 2019
Thomas Otto
T. Otto (CERN)

## Slide 13
The CDR Safety Study demonstrated that planned facilities can meet the Life Safety Objectives
Additional studies are necessary for a TDR:
  Fire Safety:
    Implementation of fire compartmentalisation
    Impact of fire scenarios on property and environment (slightly radioactive particles)
  Cryogenic Safety
    More accurate description of Helium releases
    Interaction of cold gas with smoke extraction, pressure on compartment walls
Safety Studies Proposed
Future Circular Collider Study
FCC Week 2019
Thomas Otto
18
T. Otto (CERN)

## Slide 14
Additional studies are necessary for a TDR:
  Radiation protection
    Radioactivity in experiments and beam loss points
    Management of effluents (air and water)
    Radiation monitoring programme
Precise study programme will be determined once CERN’s strategy is defined
  Specific topics in e+/e- collider
Safety Studies Proposed
Future Circular Collider Study
FCC Week 2019
Thomas Otto
19
T. Otto (CERN)

## Slide 15: FCC-hh PBD for fire safety applied to HE-LHC for validating ventilation concept
O. Rios, S. La Mendola (CERN)

## Slide 16: Conclusions
Life safety goals for occupants are reached with the baseline safety measures
Two different concepts (with and without compartments) explored.
Hot smoke extraction system can be most efficiently designed and its fire resistance lowered thanks to PBD approach.
O. Rios, S. La Mendola (CERN)
Notes: Other safety goals? Occupants safety.

## Slide 17
R2E
J. Hunt / EN-STI
Beam screen
Old
New
Latest residual gas profile
Peak power density in coils: 1.64 mW/cm3
Updated beam screen design provides less shielding for coils and cold mass.
Beam screen now absorbing ~5 % of power loss density as opposed to 16 % previously.
86 % absorbed by cold mass.
Most impacted dipole receives 278 mW/m on cold mass.
Beam-gas losses
Assumes 1015 particles/m3 as pessimistic assumption as in LHC. Finally was 200 times less.

## Slide 18
R2E Impact
J. Hunt / EN-STI
Full 214 m arc cell (axis not to scale)
FLUKA model
Some increase in dose to electronics under beamline
Updated
Previous

## Slide 19: Civil Engineering

## Slide 20
CE study progress
Spoil Management
Study of the molasses re-use (approx. 9 million cubic meters of spoil)
Samples tested from HL-LHC sites
Ongoing work:
Surface site investigation
Site investigation planning
Spoil management study
Transfer line design
Optimisation of tunnel alignment
Tunnel layout optimisation based on geology, shafts depth, construction risks and surface sites
Potential surface areas identified following first review with host states
HE-LHC
Requirements gathered from cryogenics, electrics and HVAC, which determined the modifications needed for HE-LHC for civil engineering
Cost estimate produced
CDR volumes submitted to European Strategy update for Particle Physics
Cost and schedule estimate compatible with the CDR baseline for all 3 machines: FCC-hh, FCC-ee and FCC-eh
Refinement of results (fire compartments, caverns spacing)
Additional ILF studies (cash flow, spoil volume per site, HL-LHC cost comparison)
May 2018
Dec. 2018
Aug. 2018
Sep. 2018
Jan.- June 2019
Ongoing
Future Circular Collider Study
FCC Week 2019, Brussels
Alexandra Tudora
A. Tudora, J. Osborne (CERN)

## Slide 21
Construction Schedule
Sector L-A-B : 4.5 years
Sector D-E-F : 6.5 years
Future Circular Collider Study
FCC Week 2019, Brussels
Alexandra Tudora
A. Tudora, J. Osborne (CERN)

## Slide 22
Geological uncertainty
Information near to CERN is strong due to previous experience on LEP/LHC.
Multiple deep boreholes in the area.
Vallée de l‘Arve
Mandallaz
Le Rhône
Lake Geneva
No deep borehole information available in the area.
Complex faulted region.
Molasse/limestone interface uncertain.
Moraine/molasse interface not certain, cavern close to interface.
Lack of deep boreholes in area.
Seismic and borehole information for lake crossing from proposed road tunnel, but layered nature of lake bed leads to uncertainty.
Location of the interface between molasse and molasse subalpine not certain, tunnel alignment in proximity.
Limestone formation known, but characteristics and locations of karsts unknown.
Alignment close to limestone rockhead.
The exact location and angle of the limestone/molasse interface undefined.
Future Circular Collider Study
FCC Week 2019, Brussels
Alexandra Tudora
A. Tudora, J. Osborne (CERN)

## Slide 23
Schedule for preparatory phase
A. Tudora + J. Osborne / SMB-SE
European Strategy Update 2020
CDR
Feasibility SI
(2021-2022)
Walkover survey
Geophysical investigation of all access points, Geneva Lake crossing, Rhône and Arve Valley
Principal SI (2023-2024)
Phase 1 – site investigations required for the development of preliminary design
Phase 2 – confirmation of geological profiles and engineering design parameters
Phase 3 – additional explorations needed for refined cost estimate
Types of site investigations:
Boreholes
Site testing (e.g. in-situ stress test, point load testing, SPT, CPT, permeability tests)
Rock laboratory testing (e.g. uniaxial compressive strength, petrographic studies)
Additional SI (2025-2027)
Additional data might be required after preliminary design for a more detailed geological evaluation

## Slide 24
Geodesy
Reference point coordinates for CE construction
2020 +
Accelerator information required:
Theoretical design
FCC-ee integration model
Metrology & alignment precisions
To be developed:
Geodetic surface reference Network
Reference systems and transformation algorithms
Gravity field model
Geodetic transformation software
Organisational:
Planning
Resources
CE works start
CE construction invitation to tender start
Final update of position and orientation end
Injector installation start
FCC installation start
Y8
Establish definitive reference systems end
Y3
Procure geodetic instruments start
Geodetic measurements start
Y5
Y7
Y8
Design Concept
M. Jones (CERN)

## Slide 25
Detailed integration and accessibility to be studied
FCC-ee alignment + position monitoring
CLIC
design
Concept based on design for CLIC
Full remote position monitoring
and alignment system
Wire position sensors (WPS)
Hydrostatic levelling sensors
Motorised positioning system
M. Jones (CERN)

## Slide 26
Classes of possible reuse versus landfill classes
including the probability of the prognoses in an early stage design
Concept from Brenner Base Tunnel
Excavation Materials Management

## Slide 27
… to be able to react during construction
the concept
[Dragon 2015]

## Slide 30: Host State Activities

## Slide 31: Host State Activities
Identification of activities to be carried out by project owner, by host states and by external contractors.
Ensure compatibility of the infrastructure during all lifecycle phases with socio-urbanistic and environmental requirements.
Develop administrative process schedule toward construction
Estimate impacts on the host states concerning administrative processes & financial engagements
Identification of needs for additional territorial developments for the project
Ensure participation of the population in the pre-construction phase
Ensure communication with all notified bodies and official study offices are implemented
Identify development potentials and develop plans to generate socio-economic impacts.
Accompanying of the study by SGAR (F), Etat et Canton de Genève (CH), DFAE (CH) and «mission permanente de la Suisse auprès des organisations int. à Genève»
Optimisation of the scenario in the region across France and Switzerland
Participation in the socio-economic impact studies
FCC

## Slide 32: Baseline Document Set

## Slide 33: Schedule
Challenging to be ready for construction by 2028, but still feasible
Determining factors are sequential dependencies
  Identifying and documenting a suitable placement with host state notified bodies, which still has room for adjustment during participative processes (2 yrs)
  Governmental scenario validation and débat public in France (~ 5 years)
  Zone re-classification and acquisition process in Switzerland (6 – 10 years depending on cantonal or federal sector plan procedure, foresee need to adjust plan due to oppositions)
  Débat public with preparatory phase in France (4 years) + formal processes following (enquête, DUP ca. 1.5 years)
  Provisioning of land plots to CERN in both countries (treaty)

## Slide 34: Take Home Messages
Processes need to be carried out and have to be successfully completed in both Host States, before a decision to construct can be taken.
Processes are “scenario specific”. Cannot be carried out in generic ways.
Stakeholders of both Host States actively support the processes.
Preparatory phase design project needed to carry out activities in time.
Processes take time (~ 8 years) and require the involvement of institutional and public stakeholders from 2020 onwards.
Highest priority is now to optimize the collider placement, to document the invariants and the remaining degrees of freedom to adapt. This documentation is the baseline for ”political scenario validations” in both Host States, serving officials to develop their schedules towards a construction decision by 2026.

## Slide 35
O. Martin (MAE)

## Slide 36
Conclusion
Massive political / administrative work ahead with the 2 Host States – this is only the beginning!!!
Key words
Trust
Anticipation
Environmental and legal exemplarity
Local acceptance / communication