## Sheet1
ALICE LS2 CABLES v2.1 (Oct 2017)
ID | Detector | Cable function | Voltage [V] | Current [A] | Cable reference | Diameter [mm] | Origin | Destination | Area | Connectors | Number of cables | Number of spares | Length [m] | Critical length [Y/N] | Tot length [m] | Routing defined [Y/N] | Cable trays existing [Y/N] | Requires to remove already installed cables [Y/N] | Remarks
1 | ITS | LV (PU) | 3.3 | 1 to 5 | ? | AWG10 | ITS_PP1 | PP0 | Miniframe | Orig.: tbd (connector on ITS boards: Molex 172672-2002) Dest.: tbc | 1032 | 30 | 10 | N | 10620 | N | Y | Y | Section inside the Miniframe. Connection at origin to be defined: either the ITS boards or a patch-panel
2 | ITS | LV (RU) | ? | ? | ? | AWG4 | ITS_PP1 | PP0 | Miniframe | Orig.: tbd (connector on ITS boards: Molex 172672-2002) Dest.: tbd | 32 | 4 | 10 | N | 360 | N | Y | Y | Section inside the Miniframe. Connection at origin to be defined: either the ITS boards or a patch-panel
3 | ITS | LV (BB) | ? |  | ? | AWG18 | ITS_PP1 | PP0 | Miniframe |  | 60 | 4 | 10 | N | 640 | N | Y | Y | Use multi-wire cables.
4 | ITS | Sense (RU/PU/BB) | - | - | ? | AWG22 | ITS_PP1 | PP0 | Miniframe |  | 1124 | 33 | 10 | N | 11570 | N | Y | Y | Use multi wire cables
5 | ITS | CAN bus | - | - | ? | ? | ITS_PP1 | PP0 | Miniframe |  | 16 | 4 | 10 | N | 200 | N | Y | Y | Number to be defined
6 | ITS | PT100 | - | - | ? | ? | ITS_PP1 | PP0 | Miniframe |  | ? | ? | 10 | N | ? | N | Y | Y | Number of PT100 to be defined. Define readings with Andre
7 | ITS | LV (PU) | 3.3 | 1 to 5 | ? | AWG10 | PP0 | A14-15 | A-side | Orig.: tbd Dest.: tbd (connector on CAEN A3009: APP30) | 1032 | 30 | 17 | N | 18054 | N | Y | Y | CAEN A3009 boards in destination rack.
8 | ITS | LV (RU) | ? | ? | ? | AWG4 | PP0 | A12 | A-side | Orig.: tbd Dest.: tbd (connector on CAEN A3009: APP30) | 32 | 4 | 17 | N | 612 | N | Y | Y | CAEN A3009 boards in destination rack.
9 | ITS | Sense (PU) | - | - | ? | AWG22 | PP0 | A14-15 | A-side |  | 1064 | 31 | 17 | N | 18615 | N | Y | Y | Use multi wire cables
10 | ITS | Sense (RU) | - | - | ? | AWG22 | PP0 | A12 | A-side |  | 1064 | 31 | 17 | N | 18615 | N | Y | Y | Use multi wire cables
11 | ITS | LV (BB) | ? |  | ? | AWG18 | PP0 | CR4 | A-side, PX24, CR4 |  | 60 | 4 | 92 | N | 5888 | N | Y | Y | Use multi-wire cables. CAEN SY4527 in destination rack
12 | ITS | Sense (BB) | - | - | ? | AWG22 | PP0 | CR4 | A-side, PX24, CR4 |  | 60 | 4 | 92 | N | 5888 | N | Y | Y | Use multi wire cables
13 | ITS | Control | - | - | ? | AWG14 | A14-15 | CR4 | A-side, PX24, CR4 |  | 2 | 1 | 65 | N | 195 | N | ? | N
14 | ITS | Control | - | - | ? | AWG14 | A12 | CR4 | A-side, PX24, CR4 |  | 1 | 1 | 65 | N | 130 | N | ? | N
15 | ITS | Service | - | - | ? | AWG22 | A14-15 | CR4 | A-side, PX24, CR4 |  | 2 | 1 | 65 | N | 195 | N | ? | N
16 | ITS | Service | - | - | ? | AWG22 | A12 | CR4 | A-side, PX24, CR4 |  | 1 | 1 | 65 | N | 130 | N | ? | N
17 | ITS | CAN bus | - | - | ? | ? | PP0 | CR4 | A-side, PX24, CR4 |  | 16 | 4 | 92 | N | 1840 | N | Y | Y | Number to be defined
18 | ITS | PT100 | - | - | ? | ? | PP0 | UX? | A-side, UX? |  | ? | ? | ? | N | ? | N | Y | Y | Number of PT100 to be defined. Define readings with Andre
19 | TPC | HV (A-side) | 5kV | - | 04.31.52.075.9 | 12.4 | TPC_A | PP0 | Miniframe | Orig.: 09.41.34.260.5 Dest.: ? | 18 | 2 | 10 | N | 200 | Y | N | Y | 32 HV lines/sector. New HVPS will be installed in CR4 (replacing the ISEG). Old HV cables (3x18x2) not needed
20 | TPC | Cal.pulser |  | - |  |  | TPC_A | PP0 | Miniframe | Origin (TPC A-side): Dest. (PP0): | 36 | 0 | 10 | N | 360 | Y | N | Y | These cables are already installed inside the Miniframe. They should be reinstalled if we decide to remove all the services in the Miniframe
21 | TPC | HV (A-side) | 5kV | - | 04.31.52.075.9 | 12.4 | PP0 | CR4 | A-side, PX24, CR4 | Orig.: ? Dest.: 09.41.34.268.7 | 18 | 2 | 70 | N | 1400 | Y | N | Y | 32 HV lines/sector. New HVPS will be installed in CR4 (replacing the ISEG). Old HV cables (3x18x2) not needed
22 | TPC | HV (C-side) | 5kV | - | 04.31.52.075.9 | 12.4 | TPC_C | CR4 | Backframe, C-side, O-racks, PX24, CR4 | Orig.: 09.41.34.260.5 Dest.: 09.41.34.268.7 | 18 | 2 | 110 | N | 2200 | Y | N | Y
23 | MFT | LV (digital) | 8 | 4 | ? | AWG13 | MFT_PP1 | PP0 | Miniframe | Orig.: ? Dest.: ? | 40 | 4 | 10 | N | 440 | N | N | Y
24 | MFT | LV (analog) | 8 | 1 | ? | AWG21 | MFT_PP1 | PP0 | Miniframe | Orig.: ? Dest.: ? | 40 | 4 | 10 | N | 440 | N | N | Y
25 | MFT | LV (BB) | -6 | ? | ? | AWG32 | MFT_PP1 | PP0 | Miniframe | Orig.: ? Dest.: ? | 16 | 4 | 10 | N | 200 | N | N | Y
26 | MFT | LV GBT-SCA | ? | ? | ? | AWG26 | MFT_PP1 | PP0 | Miniframe | Orig.: ? Dest.: ? | 8 | 2 | 10 | N | 100 | N | N | Y
27 | MFT | LV (digital) | 8 | 4 | ? | AWG13 | PP0 | A08-09 | A-side | Orig.: ? Dest.: PP45 1327 (red) and 1327G6 (black) (CAEN A3009) | 40 | 4 | 20 | N | 880 | N | N | Y | Power boards A3009x2
28 | MFT | LV (analog) | 8 | 1 | ? | AWG21 | PP0 | A08-09 | A-side | Orig.: ? Dest.: PP45 1327 (red) and 1327G6 (black) (CAEN A3009) | 40 | 4 | 20 | N | 880 | N | N | Y | Power boards A3009x2
29 | MFT | LV (BB) | -6 | ? | ? | AWG32 | PP0 | A08-09 | A-side | Orig.: ? Dest.: PP45 1327 (red) and 1327G6 (black) (CAEN A3006) | 16 | 4 | 20 | N | 400 | N | N | Y | Power board A3006
30 | MFT | LV GBT-SCA | ? | ? | ? | AWG26 | PP0 | A08-09 | A-side | Orig.: ? Dest.: PP45 1327 (red) and 1327G6 (black) (CAEN A3006) | 8 | 2 | 20 | N | 200 | N | N | Y | Power board A3006
31 | MFT | LV (RU) | 5 to 12 | ? | ? | ? | MFT_C | I24 | Backframe, C-side, I-racks | Orig.: same as ITS Dest.: PP45 1327 (red) and 1327G6 (black) (CAEN A3100) | ? | ? | ? | N | ? | N | N | Y | Use upper chicane (I-side) Power board: A3100 (tbc)
32 | MFT | Control | - | - | ? | AWG14 | A08-09 | CR4 (Y1 to Y6 tbc) | A-side, PX24, CR4 |  | 1 | 1 | 90 | N | 180 | N | ? | N
33 | MFT | Service | - | - | ? | AWG22 | A08-09 | CR4 (Y1 to Y6 tbc) | A-side, PX24, CR4 | Orig.: PP45 1327 (red) and 1327G6 (black) Dest.: banana | 1 | 1 | 90 | N | 180 | N | ? | N
34 | MFT | Control | - | - | ? | AWG14 | I24 | CR4 (Y1 to Y6 tbc) | I-racks, PX24, CR4 |  | 1 | 1 | 110 | N | 220 | N | ? | N
35 | MFT | Service | - | - | ? | AWG22 | I24 | CR4 (Y1 to Y6 tbc) | I-racks, PX24, CR4 | Orig.: PP45 1327 (red) and 1327G6 (black) Dest.: banana | 1 | 1 | 110 | N | 220 | N | ? | N
36 | T0A+ | HV |  |  | 04.31.51.D | 4.6 | FIT_A | PP0 | Miniframe |  | 24 | 1 | 10 | N | 250 | Y | Y | N
37 | V0+ | HV |  |  | 04.31.51.D | 4.6 | FIT_A | PP0 | Miniframe |  | 48 | 2 | 10 | N | 500 | Y | Y | N
38 | T0A+ | HV |  |  | 04.31.51.D | 4.6 | PP0 | CR4 | A-side, PX24, CR4 |  | 24 | 1 | 70 | N | 1750 | Y | Y | N
39 | V0+ | HV |  |  | 04.31.51.D | 4.6 | PP0 | CR4 | A-side, PX24, CR4 |  | 48 | 2 | 70 | N | 3500 | Y | Y | N | Possible to reuse existing V0/T0 HV cables
40 | T0C+ | HV |  |  | 04.31.51.D | 4.6 | FIT_C | CR4 | Backframe, C-side, O-racks, PX24, CR4 |  | 28 | 1 | 80 | N | 2320 | Y | Y | N
41 | T0A+ | Signal |  |  | 04.61.11.FC | 11.5 | FIT_A | C34 | L3, C-racks |  | 96 | 4 | 34 | Y | 3400 | N | N | N | Routing to be studied
42 | T0C+ | Signal |  |  | 04.61.11.FC | 11.5 | FIT_C | C34 | Backframe, C-racks |  | 112 | 4 | 33 | Y | 3828 | N | N | N | Routing to be studied
43 | V0+ | Signal |  |  | 04.61.11.E | 5 | FIT_A | C32 | L3, C-racks |  | 48 | 2 | 38 | Y | 1900 | N | N | Y | Possible to reuse existing V0/T0 signal cables (re-route V0 cables)
44 | T0A+ | Fiber (laser) |  |  | FVP100110125 | 2 | FIT_A | C33 | L3, C-racks |  | 1 | 1 | 34 | Y | 68 | N | N | Y | Existing laser fibers to be removed. This fiber is provided by detector (already connectorised)
45 | T0A+ | Fiber (laser) |  |  | 50/125 OM3 | 3 | FIT_A | C33 | L3, C-racks |  | 2 | 2 | 34 | Y | 136 | N | N | Y | Existing laser fibers to be removed
46 | T0C+ | Fiber (laser) |  |  | FVP100110125 | 2 | FIT_C | C33 | Backframe, C-racks |  | 2 | 1 | 33 | Y | 99 | N | N | Y | Existing laser fibers to be removed. This fiber is provided by detector (already connectorised)
47 | T0C+ | Fiber (laser) |  |  | 50/125 OM3 | 3 | FIT_C | C33 | Backframe, C-racks |  | 2 | 2 | 33 | Y | 132 | N | N | Y | Existing laser fibers to be removed
48 | V0+ | Fiber (laser) |  |  | 50/125 OM3 | 3 | FIT_A | C33 | L3, C-racks |  | 4 | 2 | 33 | Y | 198 | N | N | N
49 | ZDC | HV |  |  | 04.31.51.750.1 |  | ZDC-A | RA23 | LHC | 09.41.25.108.3 | 4 | 1 | 30 | N | 150 | ? | ? |  | 5 kV High-Voltage Connectors, series SHV, Female Cable Plug for crimping. 4 HV cables from the patch panel fixed to the floor in the LHC tunnel (RA23, near ZDC side A) to the service tunnel UA23, where the ZDC HV mainframe is located. We need 50 cm slack in the origin and termination places. Test required: High voltage sealing test (3000 V)
50 | ZDC | HV |  |  | 04.31.51.750.1 |  | ZDC-C | RA27 | LHC | 09.41.25.108.3 | 4 | 1 | 30 | N | 150 | ? | ? |  | 5 kV High-Voltage Connectors, series SHV, Female Cable Plug for crimping. 4 HV cables from the patch panel fixed to the floor in the LHC tunnel (RA27, near ZDC side C) to the service tunnel UA27, where the ZDC HV mainframe is located. We need 50 cm slack in the origin and termination places. Test required: High voltage sealing test (3000 V)
51 | ZDC | LVDS |  |  |  |  | CTP | CR4 | C-racks, O-racks, CR4 |  | 3 | 1 | 120 | N | 480 | ? | ? |  | Probably NOT NEEDED
52 | CPV | LV |  |  | 04.08.61.334.7 |  | CPV | A17 | A-side, L3 | 04.76.21.040.1 | 20 | 0 | 40 |  | 800 |  |  |  | 16mm2 brown
53 | MCH LV | LVDS |  |  | ? |  | CPV |  | A-side, L3 | ? |  |  |  |  | 0
54 | CPV | CTRL |  |  | 04.21.01.612.2 |  | CPV | A17 | A-side, L3 | N | 2 | 0 | 40 |  | 80
55 | MCH
MCH LV SOLAR
LV SOLAR OUTSIDE
55 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 (4 mm2) | SOL1-O-C1 | SOLC08-1-1 | C-side | Bended lug M6 on LVPS side; no connector on SOLAR crate side (cable inserted in WAGO 826-164) | 1 | 0 | 25 (tbc) | N | 0 | N | N | N | 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative; cable between LVPS and SOLAR crate
56 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL1-O-C2 | SOLC08-1-2 | C-side | Bended lug M6 on LVPS side; no connector on SOLAR crate side | 1 | 0 | 25 (tbc) | N | 0 | N | N | N | 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative; cable between LVPS and SOLAR crate
57 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL1-O-C3 | SOLC08-1-3 | C-side | Bended lug M6 on LVPS side; no connector on SOLAR crate side | 1 | 0 | 25 (tbc) | N | 0 | N | N | N | 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative; cable between LVPS and SOLAR crate
58 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL1-O-C4 | SOLC08-1-4 | C-side | Bended lug M6 on LVPS side; no connector on SOLAR crate side | 1 | 0 | 25 (tbc) | N | 0 | N | N | N | 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative; cable between LVPS and SOLAR crate
59 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL2-O-C1 | SOLC08-1-5 | C-side | Bended lug M6 on LVPS side; no connector on SOLAR crate side | 1 | 0 | 25 (tbc) | N | 0 | N | N | N | 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative; cable between LVPS and SOLAR crate
60 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL2-O-C2 | SOLC08-1-6 | C-side | Bended lug M6 on LVPS side; no connector on SOLAR crate side | 1 | 0 | 25 (tbc) | N | 0 | N | N | N | 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative; cable between LVPS and SOLAR crate
61 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL2-O-C3 | SOLC08-1-7 | C-side | Bended lug M6 on LVPS side; no connector on SOLAR crate side | 1 | 0 | 25 (tbc) | N | 0 | N | N | N | 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative; cable between LVPS and SOLAR crate
62 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL2-O-C4 | SOLC08-1-8 | C-side | Bended lug M6 on LVPS side; no connector on SOLAR crate side | 1 | 0 | 25 (tbc) | N | 0 | N | N | N | 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative; cable between LVPS and SOLAR crate
63 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL3-O-C1 | SOLC08-2-1 | C-side | Bended lug M6 on LVPS side; no connector on SOLAR crate side | 1 | 0 | 25 (tbc) | N | 0 | N | N | N | 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative; cable between LVPS and SOLAR crate
64 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL3-O-C2 | SOLC08-2-2 | C-side | Bended lug M6 on LVPS side; no connector on SOLAR crate side | 1 | 0 | 25 (tbc) | N | 0 | N | N | N | 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative; cable between LVPS and SOLAR crate
65 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL3-O-C3 | SOLC08-2-3 | C-side | Bended lug M6 on LVPS side; no connector on SOLAR crate side | 1 | 0 | 25 (tbc) | N | 0 | N | N | N | 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative; cable between LVPS and SOLAR crate
66 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL3-O-C4 | SOLC08-2-4 | C-side | Bended lug M6 on LVPS side; no connector on SOLAR crate side | 1 | 0 | 25 (tbc) | N | 0 | N | N | N | 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative; cable between LVPS and SOLAR crate
67 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL4-O-C1 | SOLC08-2-5 | C-side | Bended lug M6 on LVPS side; no connector on SOLAR crate side | 1 | 0 | 25 (tbc) | N | 0 | N | N | N | 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative; cable between LVPS and SOLAR crate
68 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL4-O-C2 | SOLC08-2-6 | C-side | Bended lug M6 on LVPS side; no connector on SOLAR crate side | 1 | 0 | 25 (tbc) | N | 0 | N | N | N | 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative; cable between LVPS and SOLAR crate
69 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL4-O-C3 | SOLC08-2-7 | C-side | Bended lug M6 on LVPS side; no connector on SOLAR crate side | 1 | 0 | 25 (tbc) | N | 0 | N | N | N | 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative; cable between LVPS and SOLAR crate
70 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL4-O-C4 | SOLC08-2-8 | C-side | Bended lug M6 on LVPS side; no connector on SOLAR crate side | 1 | 0 | 25 (tbc) | N | 0 | N | N | N | 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative; cable between LVPS and SOLAR crate
71 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL5-O-C1 | SOLC08-3-1 | C-side | Bended lug M6 on LVPS side; no connector on SOLAR crate side | 1 | 0 | 20 (tbc) | N | 0 | N | N | N | 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative; cable between LVPS and SOLAR crate
72 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL5-O-C2 | SOLC08-3-2 | C-side | Bended lug M6 on LVPS side; no connector on SOLAR crate side | 1 | 0 | 20 (tbc) | N | 0 | N | N | N | 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative; cable between LVPS and SOLAR crate
73 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL5-O-C3 | SOLC08-3-3 | C-side | Bended lug M6 on LVPS side; no connector on SOLAR crate side | 1 | 0 | 20 (tbc) | N | 0 | N | N | N | 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative; cable between LVPS and SOLAR crate
74 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL5-O-C4 | SOLC08-3-4 | C-side | Bended lug M6 on LVPS side; no connector on SOLAR crate side | 1 | 0 | 20 (tbc) | N | 0 | N | N | N | 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative; cable between LVPS and SOLAR crate
75 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL5-O-C5 | SOLC08-3-5 | C-side | Bended lug M6 on LVPS side; no connector on SOLAR crate side | 1 | 0 | 20 (tbc) | N | 0 | N | N | N | 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative; cable between LVPS and SOLAR crate
76 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL6-O-C1 | SOLC08-3-6 | C-side | Bended lug M6 on LVPS side; no connector on SOLAR crate side | 1 | 0 | 20 (tbc) | N | 0 | N | N | N | 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative; cable between LVPS and SOLAR crate
77 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL6-O-C2 | SOLC08-3-7 | C-side | Bended lug M6 on LVPS side; no connector on SOLAR crate side | 1 | 0 | 20 (tbc) | N | 0 | N | N | N | 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative; cable between LVPS and SOLAR crate
78 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL6-O-C3 | SOLC08-3-8 | C-side | Bended lug M6 on LVPS side; no connector on SOLAR crate side | 1 | 0 | 20 (tbc) | N | 0 | N | N | N | 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative; cable between LVPS and SOLAR crate
79 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL6-O-C4 | SOLC08-3-9 | C-side | Bended lug M6 on LVPS side; no connector on SOLAR crate side | 1 | 0 | 20 (tbc) | N | 0 | N | N | N | 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative; cable between LVPS and SOLAR crate
80 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL6-O-C5 | SOLC08-3-10 | C-side | Bended lug M6 on LVPS side; no connector on SOLAR crate side |  | 0 | 20 (tbc) | N | 0 | N | N | N | 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative; cable between LVPS and SOLAR crate
81 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL7-O | SOLC08-4-1 | C-side | Bended lug M6 on LVPS side; On potence side STAUBLI 7O: connector 16 pins (for 4 mm2 wires) | 1 | 0 | 15 (tbc) | N | 0 | N | N | N | 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative; cable between LVPS and bottom potence
82 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL7-O | SOLC08-4-2 | C-side | Bended lug M6 on LVPS side; On potence side STAUBLI 7O: connector 16 pins (for 4 mm2 wires) | 1 | 0 | 15 (tbc) | N | 0 | N | N | N | 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative; cable between LVPS and bottom potence
83 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL7-O | SOLC08-4-3 | C-side | Bended lug M6 on LVPS side; On potence side STAUBLI 7O: connector 16 pins (for 4 mm2 wires) | 1 | 0 | 15 (tbc) | N | 0 | N | N | N | 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative; cable between LVPS and bottom potence
84 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL7-O | SOLC08-4-4 | C-side | Bended lug M6 on LVPS side; On potence side STAUBLI 7O: connector 16 pins (for 4 mm2 wires) | 1 | 0 | 15 (tbc) | N | 0 | N | N | N | 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative; cable between LVPS and bottom potence
85 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL7-O | SOLC08-4-5 | C-side | Bended lug M6 on LVPS side; On potence side STAUBLI 7O: connector 16 pins (for 4 mm2 wires) | 1 | 0 | 15 (tbc) | N | 0 | N | N | N | 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative; cable between LVPS and bottom potence
86 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL7-O | SOLC08-4-6 | C-side | Bended lug M6 on LVPS side; On potence side STAUBLI 7O: connector 16 pins (for 4 mm2 wires) | 1 | 0 | 15 (tbc) | N | 0 | N | N | N | 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative; cable between LVPS and bottom potence
87 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL7-O | SOLC08-4-7 | C-side | Bended lug M6 on LVPS side; On potence side STAUBLI 7O: connector 16 pins (for 4 mm2 wires) | 1 | 0 | 15 (tbc) | N | 0 | N | N | N | 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative; cable between LVPS and bottom potence
88 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL8-O | SOLC08-4-8 | C-side | Bended lug M6 on LVPS side; On potence side STAUBLI 8O: connector 16 pins (for 4 mm2 wires) | 1 | 0 | 15 (tbc) | N | 0 | N | N | N | 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative; cable between LVPS and bottom potence
89 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL8-O | SOLC08-4-9 | C-side | Bended lug M6 on LVPS side; On potence side STAUBLI 8O: connector 16 pins (for 4 mm2 wires) | 1 | 0 | 15 (tbc) | N | 0 | N | N | N | 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative; cable between LVPS and bottom potence
90 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL8-O | SOLC08-4-10 | C-side | Bended lug M6 on LVPS side; On potence side STAUBLI 8O: connector 16 pins (for 4 mm2 wires) | 1 | 0 | 15 (tbc) | N | 0 | N | N | N | 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative; cable between LVPS and bottom potence
91 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL8-O | SOLC08-4-11 | C-side | Bended lug M6 on LVPS side; On potence side STAUBLI 8O: connector 16 pins (for 4 mm2 wires) | 1 | 0 | 15 (tbc) | N | 0 | N | N | N | 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative; cable between LVPS and bottom potence
92 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL8-O | SOLC08-4-12 | C-side | Bended lug M6 on LVPS side; On potence side STAUBLI 8O: connector 16 pins (for 4 mm2 wires) | 1 | 0 | 15 (tbc) | N | 0 | N | N | N | 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative; cable between LVPS and bottom potence
93 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL8-O | SOLC08-5-1 | C-side | Bended lug M6 on LVPS side; On potence side STAUBLI 8O: connector 16 pins (for 4 mm2 wires) | 1 | 0 | 15 (tbc) | N | 0 | N | N | N | 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative; cable between LVPS and bottom potence
94 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL8-O | SOLC08-5-2 | C-side | Bended lug M6 on LVPS side; On potence side STAUBLI 8O: connector 16 pins (for 4 mm2 wires) | 1 | 0 | 15 (tbc) | N | 0 | N | N | N | 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative; cable between LVPS and bottom potence
95 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL9-O | SOLC08-5-3 | C-side | Bended lug M6 on LVPS side; On potence side STAUBLI 9O: connector 16 pins (for 4 mm2 wires) | 1 | 0 | 15 (tbc) | N | 0 | N | N | N | 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative; cable between LVPS and bottom potence
96 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL9-O | SOLC08-5-4 | C-side | Bended lug M6 on LVPS side; On potence side STAUBLI 9O: connector 16 pins (for 4 mm2 wires) | 1 | 0 | 15 (tbc) | N | 0 | N | N | N | 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative; cable between LVPS and bottom potence
97 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL9-O | SOLC08-5-5 | C-side | Bended lug M6 on LVPS side; On potence side STAUBLI 9O: connector 16 pins (for 4 mm2 wires) | 1 | 0 | 15 (tbc) | N | 0 | N | N | N | 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative; cable between LVPS and bottom potence
98 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL9-O | SOLC08-5-6 | C-side | Bended lug M6 on LVPS side; On potence side STAUBLI 9O: connector 16 pins (for 4 mm2 wires) | 1 | 0 | 15 (tbc) | N | 0 | N | N | N | 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative; cable between LVPS and bottom potence
99 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL9-O | SOLC08-5-7 | C-side | Bended lug M6 on LVPS side; On potence side STAUBLI 9O: connector 16 pins (for 4 mm2 wires) | 1 | 0 | 15 (tbc) | N | 0 | N | N | N | 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative; cable between LVPS and bottom potence
100 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL9-O | SOLC08-5-8 | C-side | Bended lug M6 on LVPS side; On potence side STAUBLI 9O: connector 16 pins (for 4 mm2 wires) | 1 | 0 | 15 (tbc) | N | 0 | N | N | N | 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative; cable between LVPS and bottom potence
101 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL9-O | SOLC08-5-9 | C-side | Bended lug M6 on LVPS side; On potence side STAUBLI 9O: connector 16 pins (for 4 mm2 wires) | 1 | 0 | 15 (tbc) | N | 0 | N | N | N | 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative; cable between LVPS and bottom potence
102 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL9-O | SOLC08-5-10 | C-side | Bended lug M6 on LVPS side; On potence side STAUBLI 9O: connector 16 pins (for 4 mm2 wires) | 1 | 0 | 15 (tbc) | N | 0 | N | N | N | 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative; cable between LVPS and bottom potence
103 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL10-O | SOLC08-6-1 | C-side | Bended lug M6 on LVPS side; On potence side STAUBLI 10O: connector 16 pins (for 4 mm2 wires) | 1 | 0 | 15 (tbc) | N | 0 | N | N | N | 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative; cable between LVPS and bottom potence
104 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL10-O | SOLC08-6-2 | C-side | Bended lug M6 on LVPS side; On potence side STAUBLI 10O: connector 16 pins (for 4 mm2 wires) | 1 | 0 | 15 (tbc) | N | 0 | N | N | N | 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative; cable between LVPS and bottom potence
105 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL10-O | SOLC08-6-3 | C-side | Bended lug M6 on LVPS side; On potence side STAUBLI 10O: connector 16 pins (for 4 mm2 wires) | 1 | 0 | 15 (tbc) | N | 0 | N | N | N | 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative; cable between LVPS and bottom potence
106 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL10-O | SOLC08-6-4 | C-side | Bended lug M6 on LVPS side; On potence side STAUBLI 10O: connector 16 pins (for 4 mm2 wires) | 1 | 0 | 15 (tbc) | N | 0 | N | N | N | 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative; cable between LVPS and bottom potence
107 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL10-O | SOLC08-6-5 | C-side | Bended lug M6 on LVPS side; On potence side STAUBLI 10O: connector 16 pins (for 4 mm2 wires) | 1 | 0 | 15 (tbc) | N | 0 | N | N | N | 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative; cable between LVPS and bottom potence
108 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL10-O | SOLC08-6-6 | C-side | Bended lug M6 on LVPS side; On potence side STAUBLI 10O: connector 16 pins (for 4 mm2 wires) | 1 | 0 | 15 (tbc) | N | 0 | N | N | N | 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative; cable between LVPS and bottom potence
109 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL10-O | SOLC08-6-7 | C-side | Bended lug M6 on LVPS side; On potence side STAUBLI 10O: connector 16 pins (for 4 mm2 wires) | 1 | 0 | 15 (tbc) | N | 0 | N | N | N | 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative; cable between LVPS and bottom potence
110 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL10-O | SOLC08-6-8 | C-side | Bended lug M6 on LVPS side; On potence side STAUBLI 10O: connector 16 pins (for 4 mm2 wires) | 1 | 0 | 15 (tbc) | N | 0 | N | N | N | 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative; cable between LVPS and bottom potence
Sense SOLAR Outside
55 | MCH | Sense (SOLAR crates) |  |  | 04.21.52.104.0 (NE4) | 0.5 mm2 | SOL1-O-C1 | SOLC08-1-1 | C-side | No connector on LVPS side (cable inserted in LVPS sense connector); no connector on SOLAR crate side (cable inserted in WAGO 826-164) | 1 | 0 | 25 (tbc) | N | 0 | N | N | N | 1 cable = 2 pairs of sense = 2x2 0.5 mm2 NE4 == 1 quadrant; length is approximative; cable between LVPS and SOLAR crate
56 | MCH | Sense SOLAR |  |  | 04.21.52.104.0 (NE4) | 0.5 mm2 | SOL1-O-C2 | SOLC08-1-2 | C-side | No connector on LVPS side (cable inserted in LVPS sense connector); no connector on SOLAR crate side (cable inserted in WAGO 826-164) | 1 | 0 | 25 (tbc) | N | 0 | N | N | N | 1 cable = 2 pairs of sense = 2x2 0.5 mm2 NE4 == 1 quadrant; length is approximative; cable between LVPS and SOLAR crate
57 | MCH | Sense SOLAR |  |  | 04.21.52.104.0 (NE4) | 0.5 mm2 | SOL1-O-C3 | SOLC08-1-3 | C-side | No connector on LVPS side (cable inserted in LVPS sense connector); no connector on SOLAR crate side (cable inserted in WAGO 826-164) | 1 | 0 | 25 (tbc) | N | 0 | N | N | N | 1 cable = 2 pairs of sense = 4x0.5 mm2 NE4 == 1 quadrant; length is approximative; cable between LVPS and SOLAR crate
58 | MCH | Sense SOLAR |  |  | 04.21.52.104.0 (NE4) | 0.5 mm2 | SOL1-O-C4 | SOLC08-1-4 | C-side | No connector on LVPS side (cable inserted in LVPS sense connector); no connector on SOLAR crate side (cable inserted in WAGO 826-164) | 1 | 0 | 25 (tbc) | N | 0 | N | N | N | 1 cable = 2 pairs of sense = 2x2 0.5 mm2 NE4 == 1 quadrant; length is approximative; cable between LVPS and SOLAR crate
59 | MCH | Sense SOLAR |  |  | 04.21.52.104.0 (NE4) | 0.5 mm2 | SOL2-O-C1 | SOLC08-1-5 | C-side | No connector on LVPS side (cable inserted in LVPS sense connector); no connector on SOLAR crate side (cable inserted in WAGO 826-164) | 1 | 0 | 25 (tbc) | N | 0 | N | N | N | 1 cable = 2 pairs of sense = 2x2 0.5 mm2 NE4 == 1 quadrant; length is approximative; cable between LVPS and SOLAR crate
60 | MCH | Sense SOLAR |  |  | 04.21.52.104.0 (NE4) | 0.5 mm2 | SOL2-O-C2 | SOLC08-1-6 | C-side | No connector on LVPS side (cable inserted in LVPS sense connector); no connector on SOLAR crate side (cable inserted in WAGO 826-164) | 1 | 0 | 25 (tbc) | N | 0 | N | N | N | 1 cable = 2 pairs of sense = 2x2 0.5 mm2 NE4 == 1 quadrant; length is approximative; cable between LVPS and SOLAR crate
61 | MCH | Sense SOLAR |  |  | 04.21.52.104.0 (NE4) | 0.5 mm2 | SOL2-O-C3 | SOLC08-1-7 | C-side | No connector on LVPS side (cable inserted in LVPS sense connector); no connector on SOLAR crate side (cable inserted in WAGO 826-164) | 1 | 0 | 25 (tbc) | N | 0 | N | N | N | 1 cable = 2 pairs of sense = 2x2 0.5 mm2 NE4 == 1 quadrant; length is approximative; cable between LVPS and SOLAR crate
62 | MCH | Sense SOLAR |  |  | 04.21.52.104.0 (NE4) | 0.5 mm2 | SOL2-O-C4 | SOLC08-1-8 | C-side | No connector on LVPS side (cable inserted in LVPS sense connector); no connector on SOLAR crate side (cable inserted in WAGO 826-164) | 1 | 0 | 25 (tbc) | N | 0 | N | N | N | 1 cable = 2 pairs of sense = 2x2 0.5 mm2 NE4 == 1 quadrant; length is approximative; cable between LVPS and SOLAR crate
63 | MCH | Sense SOLAR |  |  | 04.21.52.104.0 (NE4) | 0.5 mm2 | SOL3-O-C1 | SOLC08-2-1 | C-side | No connector on LVPS side (cable inserted in LVPS sense connector); no connector on SOLAR crate side (cable inserted in WAGO 826-164) | 1 | 0 | 25 (tbc) | N | 0 | N | N | N | 1 cable = 2 pairs of sense = 2x2 0.5 mm2 NE4 == 1 quadrant; length is approximative; cable between LVPS and SOLAR crate
64 | MCH | Sense SOLAR |  |  | 04.21.52.104.0 (NE4) | 0.5 mm2 | SOL3-O-C2 | SOLC08-2-2 | C-side | No connector on LVPS side (cable inserted in LVPS sense connector); no connector on SOLAR crate side (cable inserted in WAGO 826-164) | 1 | 0 | 25 (tbc) | N | 0 | N | N | N | 1 cable = 2 pairs of sense = 2x2 0.5 mm2 NE4 == 1 quadrant; length is approximative; cable between LVPS and SOLAR crate
65 | MCH | Sense SOLAR |  |  | 04.21.52.104.0 (NE4) | 0.5 mm2 | SOL3-O-C3 | SOLC08-2-3 | C-side | No connector on LVPS side (cable inserted in LVPS sense connector); no connector on SOLAR crate side (cable inserted in WAGO 826-164) | 1 | 0 | 25 (tbc) | N | 0 | N | N | N | 1 cable = 2 pairs of sense = 2x2 0.5 mm2 NE4 == 1 quadrant; length is approximative; cable between LVPS and SOLAR crate
66 | MCH | Sense SOLAR |  |  | 04.21.52.104.0 (NE4) | 0.5 mm2 | SOL3-O-C4 | SOLC08-2-4 | C-side | No connector on LVPS side (cable inserted in LVPS sense connector); no connector on SOLAR crate side (cable inserted in WAGO 826-164) | 1 | 0 | 25 (tbc) | N | 0 | N | N | N | 1 cable = 2 pairs of sense = 2x2 0.5 mm2 NE4 == 1 quadrant; length is approximative; cable between LVPS and SOLAR crate
67 | MCH | Sense SOLAR |  |  | 04.21.52.104.0 (NE4) | 0.5 mm2 | SOL4-O-C1 | SOLC08-2-5 | C-side | No connector on LVPS side (cable inserted in LVPS sense connector); no connector on SOLAR crate side (cable inserted in WAGO 826-164) | 1 | 0 | 25 (tbc) | N | 0 | N | N | N | 1 cable = 2 pairs of sense = 2x2 0.5 mm2 NE4 == 1 quadrant; length is approximative; cable between LVPS and SOLAR crate
68 | MCH | Sense SOLAR |  |  | 04.21.52.104.0 (NE4) | 0.5 mm2 | SOL4-O-C2 | SOLC08-2-6 | C-side | No connector on LVPS side (cable inserted in LVPS sense connector); no connector on SOLAR crate side (cable inserted in WAGO 826-164) | 1 | 0 | 25 (tbc) | N | 0 | N | N | N | 1 cable = 2 pairs of sense = 2x2 0.5 mm2 NE4 == 1 quadrant; length is approximative; cable between LVPS and SOLAR crate
69 | MCH | Sense SOLAR |  |  | 04.21.52.104.0 (NE4) | 0.5 mm2 | SOL4-O-C3 | SOLC08-2-7 | C-side | No connector on LVPS side (cable inserted in LVPS sense connector); no connector on SOLAR crate side (cable inserted in WAGO 826-164) | 1 | 0 | 25 (tbc) | N | 0 | N | N | N | 1 cable = 2 pairs of sense = 2x2 0.5 mm2 NE4 == 1 quadrant; length is approximative; cable between LVPS and SOLAR crate
70 | MCH | Sense SOLAR |  |  | 04.21.52.104.0 (NE4) | 0.5 mm2 | SOL4-O-C4 | SOLC08-2-8 | C-side | No connector on LVPS side (cable inserted in LVPS sense connector); no connector on SOLAR crate side (cable inserted in WAGO 826-164) | 1 | 0 | 25 (tbc) | N | 0 | N | N | N | 1 cable = 2 pairs of sense = 2x2 0.5 mm2 NE4 == 1 quadrant; length is approximative; cable between LVPS and SOLAR crate
71 | MCH | Sense SOLAR |  |  | 04.21.52.120.8 (NE10) | 0.5 mm2 | SOL5-O-C1 | SOLC08-3-1 | C-side | No connector on LVPS side (cable inserted in LVPS sense connector); no connector on SOLAR crate side (cable inserted in WAGO 826-164) | 1 | 0 | 20 (tbc) | N | 0 | N | N | N | 1 cable = 5 pairs of sense = 5x2 0.5 mm2 NE10 == 1 half-chamber station 3; length is approximative; cable between LVPS and SOLAR crate
72 | MCH | Sense SOLAR |  |  | 04.21.52.120.8 (NE10) | 0.5 mm2 | SOL5-O-C2 | SOLC08-3-2 | C-side | No connector on LVPS side (cable inserted in LVPS sense connector); no connector on SOLAR crate side (cable inserted in WAGO 826-164) | 1 | 0 | 20 (tbc) | N | 0 | N | N | N | 1 cable = 5 pairs of sense = 5x2 0.5 mm2 NE10 == 1 half-chamber station 3; length is approximative; cable between LVPS and SOLAR crate
73 | MCH | Sense SOLAR |  |  | 04.21.52.120.8 (NE10) | 0.5 mm2 | SOL5-O-C3 | SOLC08-3-3 | C-side | No connector on LVPS side (cable inserted in LVPS sense connector); no connector on SOLAR crate side (cable inserted in WAGO 826-164) | 1 | 0 | 20 (tbc) | N | 0 | N | N | N | 1 cable = 5 pairs of sense = 5x2 0.5 mm2 NE10 == 1 half-chamber station 3; length is approximative; cable between LVPS and SOLAR crate
74 | MCH | Sense SOLAR |  |  | 04.21.52.120.8 (NE10) | 0.5 mm2 | SOL5-O-C4 | SOLC08-3-4 | C-side | No connector on LVPS side (cable inserted in LVPS sense connector); no connector on SOLAR crate side (cable inserted in WAGO 826-164) | 1 | 0 | 20 (tbc) | N | 0 | N | N | N | 1 cable = 5 pairs of sense = 5x2 0.5 mm2 NE10 == 1 half-chamber station 3; length is approximative; cable between LVPS and SOLAR crate
75 | MCH | Sense SOLAR |  |  | 04.21.52.120.8 (NE10) | 0.5 mm2 | SOL5-O-C5 | SOLC08-3-5 | C-side | No connector on LVPS side (cable inserted in LVPS sense connector); no connector on SOLAR crate side (cable inserted in WAGO 826-164) | 1 | 0 | 20 (tbc) | N | 0 | N | N | N | 1 cable = 5 pairs of sense = 5x2 0.5 mm2 NE10 == 1 half-chamber station 3; length is approximative; cable between LVPS and SOLAR crate
76 | MCH | Sense SOLAR |  |  | 04.21.52.120.8 (NE10) | 0.5 mm2 | SOL6-O-C1 | SOLC08-3-6 | C-side | No connector on LVPS side (cable inserted in LVPS sense connector); no connector on SOLAR crate side (cable inserted in WAGO 826-164) | 1 | 0 | 20 (tbc) | N | 0 | N | N | N | 1 cable = 5 pairs of sense = 5x2 0.5 mm2 NE10 == 1 half-chamber station 3; length is approximative; cable between LVPS and SOLAR crate
77 | MCH | Sense SOLAR |  |  | 04.21.52.120.8 (NE10) | 0.5 mm2 | SOL6-O-C2 | SOLC08-3-7 | C-side | No connector on LVPS side (cable inserted in LVPS sense connector); no connector on SOLAR crate side (cable inserted in WAGO 826-164) | 1 | 0 | 20 (tbc) | N | 0 | N | N | N | 1 cable = 5 pairs of sense = 5x2 0.5 mm2 NE10 == 1 half-chamber station 3; length is approximative; cable between LVPS and SOLAR crate
78 | MCH | Sense SOLAR |  |  | 04.21.52.120.8 (NE10) | 0.5 mm2 | SOL6-O-C3 | SOLC08-3-8 | C-side | No connector on LVPS side (cable inserted in LVPS sense connector); no connector on SOLAR crate side (cable inserted in WAGO 826-164) | 1 | 0 | 20 (tbc) | N | 0 | N | N | N | 1 cable = 5 pairs of sense = 5x2 0.5 mm2 NE10 == 1 half-chamber station 3; length is approximative; cable between LVPS and SOLAR crate
79 | MCH | Sense SOLAR |  |  | 04.21.52.120.8 (NE10) | 0.5 mm2 | SOL6-O-C4 | SOLC08-3-9 | C-side | No connector on LVPS side (cable inserted in LVPS sense connector); no connector on SOLAR crate side (cable inserted in WAGO 826-164) | 1 | 0 | 20 (tbc) | N | 0 | N | N | N | 1 cable = 5 pairs of sense = 5x2 0.5 mm2 NE10 == 1 half-chamber station 3; length is approximative; cable between LVPS and SOLAR crate
80 | MCH | Sense SOLAR |  |  | 04.21.52.120.8 (NE10) | 0.5 mm2 | SOL6-O-C5 | SOLC08-3-10 | C-side | No connector on LVPS side (cable inserted in LVPS sense connector); no connector on SOLAR crate side (cable inserted in WAGO 826-164) |  | 0 | 20 (tbc) | N | 0 | N | N | N | 1 cable = 5 pairs of sense = 5x2 0.5 mm2 NE10 == 1 half-chamber station 3; length is approximative; cable between LVPS and SOLAR crate
81 | MCH | Sense SOLAR |  |  | 04.21.52.130.6 (NE18) | 0.5 mm2 | SOL7-O | SOLC08-4-1 | C-side | No connector on LVPS side (cable inserted in LVPS sense connector); BURNDY 16 pins on potence side 7O | 1 | 0 | 15 (tbc) | N | 0 | N | N | N | 1 cable = 9 pairs of sense = 9x2 0.5 mm2 NE18 == 1 half-chamber station 4; length is approximative; cable between LVPS and potence
82 | MCH | Sense SOLAR |  |  | 04.21.52.130.6 (NE18) | 0.5 mm2 | SOL7-O | SOLC08-4-2 | C-side | No connector on LVPS side (cable inserted in LVPS sense connector); BURNDY on potence side 7O | 1 | 0 | 15 (tbc) | N | 0 | N | N | N | 1 cable = 9 pairs of sense = 9x2 0.5 mm2 NE18 == 1 half-chamber station 4; length is approximative; cable between LVPS and potence
83 | MCH | Sense SOLAR |  |  | 04.21.52.130.6 (NE18) | 0.5 mm2 | SOL7-O | SOLC08-4-3 | C-side | No connector on LVPS side (cable inserted in LVPS sense connector); BURNDY on potence side 7O | 1 | 0 | 15 (tbc) | N | 0 | N | N | N | 1 cable = 9 pairs of sense = 9x2 0.5 mm2 NE18 == 1 half-chamber station 4; length is approximative; cable between LVPS and potence
84 | MCH | Sense SOLAR |  |  | 04.21.52.130.6 (NE18) | 0.5 mm2 | SOL7-O | SOLC08-4-4 | C-side | No connector on LVPS side (cable inserted in LVPS sense connector); BURNDY on potence side 7O | 1 | 0 | 15 (tbc) | N | 0 | N | N | N | 1 cable = 9 pairs of sense = 9x2 0.5 mm2 NE18 == 1 half-chamber station 4; length is approximative; cable between LVPS and potence
85 | MCH | Sense SOLAR |  |  | 04.21.52.130.6 (NE18) | 0.5 mm2 | SOL7-O | SOLC08-4-5 | C-side | No connector on LVPS side (cable inserted in LVPS sense connector); BURNDY on potence side 7O | 1 | 0 | 15 (tbc) | N | 0 | N | N | N | 1 cable = 9 pairs of sense = 9x2 0.5 mm2 NE18 == 1 half-chamber station 4; length is approximative; cable between LVPS and potence
86 | MCH | Sense SOLAR |  |  | 04.21.52.130.6 (NE18) | 0.5 mm2 | SOL7-O | SOLC08-4-6 | C-side | No connector on LVPS side (cable inserted in LVPS sense connector); BURNDY on potence side 7O | 1 | 0 | 15 (tbc) | N | 0 | N | N | N | 1 cable = 9 pairs of sense = 9x2 0.5 mm2 NE18 == 1 half-chamber station 4; length is approximative; cable between LVPS and potence
87 | MCH | Sense SOLAR |  |  | 04.21.52.130.6 (NE18) | 0.5 mm2 | SOL7-O | SOLC08-4-7 | C-side | No connector on LVPS side (cable inserted in LVPS sense connector); BURNDY on potence side 7O | 1 | 0 | 15 (tbc) | N | 0 | N | N | N | 1 cable = 9 pairs of sense = 9x2 0.5 mm2 NE18 == 1 half-chamber station 4; length is approximative; cable between LVPS and potence
88 | MCH | Sense SOLAR |  |  | 04.21.52.130.6 (NE18) | 0.5 mm2 | SOL8-O | SOLC08-4-8 | C-side | No connector on LVPS side (cable inserted in LVPS sense connector); BURNDY on potence side 7O | 1 | 0 | 15 (tbc) | N | 0 | N | N | N | 1 cable = 9 pairs of sense = 9x2 0.5 mm2 NE18 == 1 half-chamber station 4; length is approximative; cable between LVPS and potence
89 | MCH | Sense SOLAR |  |  | 04.21.52.130.6 (NE18) | 0.5 mm2 | SOL8-O | SOLC08-4-9 | C-side | No connector on LVPS side (cable inserted in LVPS sense connector); BURNDY on potence side 8O | 1 | 0 | 15 (tbc) | N | 0 | N | N | N | 1 cable = 9 pairs of sense = 9x2 0.5 mm2 NE18 == 1 half-chamber station 4; length is approximative; cable between LVPS and potence
90 | MCH | Sense SOLAR |  |  | 04.21.52.130.6 (NE18) | 0.5 mm2 | SOL8-O | SOLC08-4-10 | C-side | No connector on LVPS side (cable inserted in LVPS sense connector); BURNDY on potence side 8O | 1 | 0 | 15 (tbc) | N | 0 | N | N | N | 1 cable = 9 pairs of sense = 9x2 0.5 mm2 NE18 == 1 half-chamber station 4; length is approximative; cable between LVPS and potence
91 | MCH | Sense SOLAR |  |  | 04.21.52.130.6 (NE18) | 0.5 mm2 | SOL8-O | SOLC08-4-11 | C-side | No connector on LVPS side (cable inserted in LVPS sense connector); BURNDY on potence side 8O | 1 | 0 | 15 (tbc) | N | 0 | N | N | N | 1 cable = 9 pairs of sense = 9x2 0.5 mm2 NE18 == 1 half-chamber station 4; length is approximative; cable between LVPS and potence
92 | MCH | Sense SOLAR |  |  | 04.21.52.130.6 (NE18) | 0.5 mm2 | SOL8-O | SOLC08-4-12 | C-side | No connector on LVPS side (cable inserted in LVPS sense connector); BURNDY on potence side 8O | 1 | 0 | 15 (tbc) | N | 0 | N | N | N | 1 cable = 9 pairs of sense = 9x2 0.5 mm2 NE18 == 1 half-chamber station 4; length is approximative; cable between LVPS and potence
93 | MCH | Sense SOLAR |  |  | 04.21.52.130.6 (NE18) | 0.5 mm2 | SOL8-O | SOLC08-5-1 | C-side | No connector on LVPS side (cable inserted in LVPS sense connector); BURNDY on potence side 8O | 1 | 0 | 15 (tbc) | N | 0 | N | N | N | 1 cable = 9 pairs of sense = 9x2 0.5 mm2 NE18 == 1 half-chamber station 4; length is approximative; cable between LVPS and potence
94 | MCH | Sense SOLAR |  |  | 04.21.52.130.6 (NE18) | 0.5 mm2 | SOL8-O | SOLC08-5-2 | C-side | No connector on LVPS side (cable inserted in LVPS sense connector); BURNDY on potence side 8O | 1 | 0 | 15 (tbc) | N | 0 | N | N | N | 1 cable = 9 pairs of sense = 9x2 0.5 mm2 NE18 == 1 half-chamber station 4; length is approximative; cable between LVPS and potence
95 | MCH | Sense SOLAR |  |  | 04.21.52.130.6 (NE18) | 0.5 mm2 | SOL9-O | SOLC08-5-3 | C-side | No connector on LVPS side (cable inserted in LVPS sense connector); BURNDY on potence side 9O | 1 | 0 | 15 (tbc) | N | 0 | N | N | N | 1 cable = 9 pairs of sense = 9x2 0.5 mm2 NE18 == 1 half-chamber station 5; length is approximative; cable between LVPS and potence
96 | MCH | Sense SOLAR |  |  | 04.21.52.130.6 (NE18) | 0.5 mm2 | SOL9-O | SOLC08-5-4 | C-side | No connector on LVPS side (cable inserted in LVPS sense connector); BURNDY on potence side 9O | 1 | 0 | 15 (tbc) | N | 0 | N | N | N | 1 cable = 9 pairs of sense = 9x2 0.5 mm2 NE18 == 1 half-chamber station 5; length is approximative; cable between LVPS and potence
97 | MCH | Sense SOLAR |  |  | 04.21.52.130.6 (NE18) | 0.5 mm2 | SOL9-O | SOLC08-5-5 | C-side | No connector on LVPS side (cable inserted in LVPS sense connector); BURNDY on potence side 9O | 1 | 0 | 15 (tbc) | N | 0 | N | N | N | 1 cable = 9 pairs of sense = 9x2 0.5 mm2 NE18 == 1 half-chamber station 5; length is approximative; cable between LVPS and potence
98 | MCH | Sense SOLAR |  |  | 04.21.52.130.6 (NE18) | 0.5 mm2 | SOL9-O | SOLC08-5-6 | C-side | No connector on LVPS side (cable inserted in LVPS sense connector); BURNDY on potence side 9O | 1 | 0 | 15 (tbc) | N | 0 | N | N | N | 1 cable = 9 pairs of sense = 9x2 0.5 mm2 NE18 == 1 half-chamber station 5; length is approximative; cable between LVPS and potence
99 | MCH | Sense SOLAR |  |  | 04.21.52.130.6 (NE18) | 0.5 mm2 | SOL9-O | SOLC08-5-7 | C-side | No connector on LVPS side (cable inserted in LVPS sense connector); BURNDY on potence side 9O | 1 | 0 | 15 (tbc) | N | 0 | N | N | N | 1 cable = 9 pairs of sense = 9x2 0.5 mm2 NE18 == 1 half-chamber station 5; length is approximative; cable between LVPS and potence
100 | MCH | Sense SOLAR |  |  | 04.21.52.130.6 (NE18) | 0.5 mm2 | SOL9-O | SOLC08-5-8 | C-side | No connector on LVPS side (cable inserted in LVPS sense connector); BURNDY on potence side 9O | 1 | 0 | 15 (tbc) | N | 0 | N | N | N | 1 cable = 9 pairs of sense = 9x2 0.5 mm2 NE18 == 1 half-chamber station 5; length is approximative; cable between LVPS and potence
101 | MCH | Sense SOLAR |  |  | 04.21.52.130.6 (NE18) | 0.5 mm2 | SOL9-O | SOLC08-5-9 | C-side | No connector on LVPS side (cable inserted in LVPS sense connector); BURNDY on potence side 9O | 1 | 0 | 15 (tbc) | N | 0 | N | N | N | 1 cable = 9 pairs of sense = 9x2 0.5 mm2 NE18 == 1 half-chamber station 5; length is approximative; cable between LVPS and potence
102 | MCH | Sense SOLAR |  |  | 04.21.52.130.6 (NE18) | 0.5 mm2 | SOL9-O | SOLC08-5-10 | C-side | No connector on LVPS side (cable inserted in LVPS sense connector); BURNDY on potence side 9O | 1 | 0 | 15 (tbc) | N | 0 | N | N | N | 1 cable = 9 pairs of sense = 9x2 0.5 mm2 NE18 == 1 half-chamber station 5; length is approximative; cable between LVPS and potence
103 | MCH | Sense SOLAR |  |  | 04.21.52.130.6 (NE18) | 0.5 mm2 | SOL10-O | SOLC08-6-1 | C-side | No connector on LVPS side (cable inserted in LVPS sense connector); BURNDY on potence side 10O | 1 | 0 | 15 (tbc) | N | 0 | N | N | N | 1 cable = 9 pairs of sense = 9x2 0.5 mm2 NE18 == 1 half-chamber station 5; length is approximative; cable between LVPS and potence
104 | MCH | Sense SOLAR |  |  | 04.21.52.130.6 (NE18) | 0.5 mm2 | SOL10-O | SOLC08-6-2 | C-side | No connector on LVPS side (cable inserted in LVPS sense connector); BURNDY on potence side 10O | 1 | 0 | 15 (tbc) | N | 0 | N | N | N | 1 cable = 9 pairs of sense = 9x2 0.5 mm2 NE18 == 1 half-chamber station 5; length is approximative; cable between LVPS and potence
105 | MCH | Sense SOLAR |  |  | 04.21.52.130.6 (NE18) | 0.5 mm2 | SOL10-O | SOLC08-6-3 | C-side | No connector on LVPS side (cable inserted in LVPS sense connector); BURNDY on potence side 10O | 1 | 0 | 15 (tbc) | N | 0 | N | N | N | 1 cable = 9 pairs of sense = 9x2 0.5 mm2 NE18 == 1 half-chamber station 5; length is approximative; cable between LVPS and potence
106 | MCH | Sense SOLAR |  |  | 04.21.52.130.6 (NE18) | 0.5 mm2 | SOL10-O | SOLC08-6-4 | C-side | No connector on LVPS side (cable inserted in LVPS sense connector); BURNDY on potence side 10O | 1 | 0 | 15 (tbc) | N | 0 | N | N | N | 1 cable = 9 pairs of sense = 9x2 0.5 mm2 NE18 == 1 half-chamber station 5; length is approximative; cable between LVPS and potence
107 | MCH | Sense SOLAR |  |  | 04.21.52.130.6 (NE18) | 0.5 mm2 | SOL10-O | SOLC08-6-5 | C-side | No connector on LVPS side (cable inserted in LVPS sense connector); BURNDY on potence side 10O | 1 | 0 | 15 (tbc) | N | 0 | N | N | N | 1 cable = 9 pairs of sense = 9x2 0.5 mm2 NE18 == 1 half-chamber station 5; length is approximative; cable between LVPS and potence
108 | MCH | Sense SOLAR |  |  | 04.21.52.130.6 (NE18) | 0.5 mm2 | SOL10-O | SOLC08-6-6 | C-side | No connector on LVPS side (cable inserted in LVPS sense connector); BURNDY on potence side 10O | 1 | 0 | 15 (tbc) | N | 0 | N | N | N | 1 cable = 9 pairs of sense = 9x2 0.5 mm2 NE18 == 1 half-chamber station 5; length is approximative; cable between LVPS and potence
109 | MCH | Sense SOLAR |  |  | 04.21.52.130.6 (NE18) | 0.5 mm2 | SOL10-O | SOLC08-6-7 | C-side | No connector on LVPS side (cable inserted in LVPS sense connector); BURNDY on potence side 10O | 1 | 0 | 15 (tbc) | N | 0 | N | N | N | 1 cable = 9 pairs of sense = 9x2 0.5 mm2 NE18 == 1 half-chamber station 5; length is approximative; cable between LVPS and potence
110 | MCH | Sense SOLAR |  |  | 04.21.52.130.6 (NE18) | 0.5 mm2 | SOL10-O | SOLC08-6-8 | C-side | No connector on LVPS side (cable inserted in LVPS sense connector); BURNDY on potence side 10O | 1 | 0 | 15 (tbc) | N | 0 | N | N | N | 1 cable = 9 pairs of sense = 9x2 0.5 mm2 NE18 == 1 half-chamber station 5; length is approximative; cable between LVPS and potence
LV SOLAR on potence OUTSIDE
197 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL7-O | SOL7-O-C1 | C-side | On potence side STAUBLI 7O: connector 16 pins (for 4 mm2 wires); no connector on SOLAR crate side (cable inserted in WAGO 826-164) | 1 | 0 | 4,5 (tbc) | N | 0 | N | N | N | cable on CH7O potence (Station 4): 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative ; cable between Bottom Potence and SOLAR crate
198 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL7-O | SOL7-O-C2 | C-side | On potence side STAUBLI 7O: connector 16 pins (for 4 mm2 wires); no connector on SOLAR crate side (cable inserted in WAGO 826-164) | 1 | 0 | 4 (tbc) | N | 0 | N | N | N | cable on CH7O potence (Station 4): 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative ; cable between Bottom Potence and SOLAR crate
199 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL7-O | SOL7-O-C3 | C-side | On potence side STAUBLI 7O: connector 16 pins (for 4 mm2 wires); no connector on SOLAR crate side (cable inserted in WAGO 826-164) | 1 | 0 | 3,5 (tbc) | N | 0 | N | N | N | cable on CH7O potence (Station 4): 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative ; cable between Bottom Potence and SOLAR crate
200 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL7-O | SOL7-O-C4 | C-side | On potence side STAUBLI 7O: connector 16 pins (for 4 mm2 wires); no connector on SOLAR crate side (cable inserted in WAGO 826-164) | 1 | 0 | 3 (tbc) | N | 0 | N | N | N | cable on CH7O potence (Station 4): 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative ; cable between Bottom Potence and SOLAR crate
201 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL7-O | SOL7-O-C5 | C-side | On potence side STAUBLI 7O: connector 16 pins (for 4 mm2 wires); no connector on SOLAR crate side (cable inserted in WAGO 826-164) | 1 | 0 | 2,5 (tbc) | N | 0 | N | N | N | cable on CH7O potence (Station 4): 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative ; cable between Bottom Potence and SOLAR crate
202 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL7-O | SOL7-O-C6 | C-side | On potence side STAUBLI 7O: connector 16 pins (for 4 mm2 wires); no connector on SOLAR crate side (cable inserted in WAGO 826-164) | 1 | 0 | 2 (tbc) | N | 0 | N | N | N | cable on CH7O potence (Station 4): 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative ; cable between Bottom Potence and SOLAR crate
203 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL7-O | SOL7-O-C7 | C-side | On potence side STAUBLI 7O: connector 16 pins (for 4 mm2 wires); no connector on SOLAR crate side (cable inserted in WAGO 826-164) | 1 | 0 | 1,5 (tbc) | N | 0 | N | N | N | cable on CH7O potence (Station 4): 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative ; cable between Bottom Potence and SOLAR crate
204 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL8-O | SOL8-O-C1 | C-side | On potence side STAUBLI 8O: connector 16 pins (for 4 mm2 wires); no connector on SOLAR crate side (cable inserted in WAGO 826-164) | 1 | 0 | 4,5 (tbc) | N | 0 | N | N | N | cable on CH8O potence (Station 4): 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative ; cable between Bottom Potence and SOLAR crate
205 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL8-O | SOL8-O-C2 | C-side | On potence side STAUBLI 8O: connector 16 pins (for 4 mm2 wires); no connector on SOLAR crate side (cable inserted in WAGO 826-164) | 1 | 0 | 4 (tbc) | N | 0 | N | N | N | cable on CH8O potence (Station 4): 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative ; cable between Bottom Potence and SOLAR crate
206 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL8-O | SOL8-O-C3 | C-side | On potence side STAUBLI 8O: connector 16 pins (for 4 mm2 wires); no connector on SOLAR crate side (cable inserted in WAGO 826-164) | 1 | 0 | 3,5 (tbc) | N | 0 | N | N | N | cable on CH8O potence (Station 4): 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative ; cable between Bottom Potence and SOLAR crate
207 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL8-O | SOL8-O-C4 | C-side | On potence side STAUBLI 8O: connector 16 pins (for 4 mm2 wires); no connector on SOLAR crate side (cable inserted in WAGO 826-164) | 1 | 0 | 3 (tbc) | N | 0 | N | N | N | cable on CH8O potence (Station 4): 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative ; cable between Bottom Potence and SOLAR crate
208 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL8-O | SOL8-O-C5 | C-side | On potence side STAUBLI 8O: connector 16 pins (for 4 mm2 wires); no connector on SOLAR crate side (cable inserted in WAGO 826-164) | 1 | 0 | 2,5 (tbc) | N | 0 | N | N | N | cable on CH8O potence (Station 4): 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative ; cable between Bottom Potence and SOLAR crate
209 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL8-O | SOL8-O-C6 | C-side | On potence side STAUBLI 8O: connector 16 pins (for 4 mm2 wires); no connector on SOLAR crate side (cable inserted in WAGO 826-164) | 1 | 0 | 2 (tbc) | N | 0 | N | N | N | cable on CH8O potence (Station 4): 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative ; cable between Bottom Potence and SOLAR crate
210 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL8-O | SOL8-O-C7 | C-side | On potence side STAUBLI 8O: connector 16 pins (for 4 mm2 wires); no connector on SOLAR crate side (cable inserted in WAGO 826-164) | 1 | 0 | 1,5 (tbc) | N | 0 | N | N | N | cable on CH8O potence (Station 4): 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative ; cable between Bottom Potence and SOLAR crate
211 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL9-O | SOL9-O-C1 | C-side | On potence side STAUBLI 9O: connector 16 pins (for 4 mm2 wires); no connector on SOLAR crate side (cable inserted in WAGO 826-164) | 1 | 0 | 5 (tbc) | N | 0 | N | N | N | cable on CH9O potence (Station 5): 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative ; cable between Bottom Potence and SOLAR crate
212 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL9-O | SOL9-O-C2 | C-side | On potence side STAUBLI 9O: connector 16 pins (for 4 mm2 wires); no connector on SOLAR crate side (cable inserted in WAGO 826-164) | 1 | 0 | 4,5 (tbc) | N | 0 | N | N | N | cable on CH9O potence (Station 5): 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative ; cable between Bottom Potence and SOLAR crate
213 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL9-O | SOL9-O-C3 | C-side | On potence side STAUBLI 9O: connector 16 pins (for 4 mm2 wires); no connector on SOLAR crate side (cable inserted in WAGO 826-164) | 1 | 0 | 4 (tbc) | N | 0 | N | N | N | cable on CH9O potence (Station 5): 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative ; cable between Bottom Potence and SOLAR crate
214 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL9-O | SOL9-O-C4 | C-side | On potence side STAUBLI 9O: connector 16 pins (for 4 mm2 wires); no connector on SOLAR crate side (cable inserted in WAGO 826-164) | 1 | 0 | 3,5 (tbc) | N | 0 | N | N | N | cable on CH9O potence (Station 5): 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative ; cable between Bottom Potence and SOLAR crate
215 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL9-O | SOL9-O-C5 | C-side | On potence side STAUBLI 9O: connector 16 pins (for 4 mm2 wires); no connector on SOLAR crate side (cable inserted in WAGO 826-164) | 1 | 0 | 3 (tbc) | N | 0 | N | N | N | cable on CH9O potence (Station 5): 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative ; cable between Bottom Potence and SOLAR crate
216 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL9-O | SOL9-O-C6 | C-side | On potence side STAUBLI 9O: connector 16 pins (for 4 mm2 wires); no connector on SOLAR crate side (cable inserted in WAGO 826-164) | 1 | 0 | 2,5 (tbc) | N | 0 | N | N | N | cable on CH9O potence (Station 5): 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative ; cable between Bottom Potence and SOLAR crate
217 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL9-O | SOL9-O-C7 | C-side | On potence side STAUBLI 9O: connector 16 pins (for 4 mm2 wires); no connector on SOLAR crate side (cable inserted in WAGO 826-164) | 1 | 0 | 2 (tbc) | N | 0 | N | N | N | cable on CH9O potence (Station 5): 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative ; cable between Bottom Potence and SOLAR crate
218 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL9-O | SOL9-O-C8 | C-side | On potence side STAUBLI 9O: connector 16 pins (for 4 mm2 wires); no connector on SOLAR crate side (cable inserted in WAGO 826-164) | 1 | 0 | 1,5 (tbc) | N | 0 | N | N | N | cable on CH9O potence (Station 5): 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative ; cable between Bottom Potence and SOLAR crate
219 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL10-O | SOL10-O-C1 | C-side | On potence side STAUBLI 10O: connector 16 pins (for 4 mm2 wires); no connector on SOLAR crate side (cable inserted in WAGO 826-164) | 1 | 0 | 5 (tbc) | N | 0 | N | N | N | cable on CH10O potence (Station 5): 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative ; cable between Bottom Potence and SOLAR crate
220 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL10-O | SOL10-O-C2 | C-side | On potence side STAUBLI 10O: connector 16 pins (for 4 mm2 wires); no connector on SOLAR crate side (cable inserted in WAGO 826-164) | 1 | 0 | 4,5 (tbc) | N | 0 | N | N | N | cable on CH10O potence (Station 5): 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative ; cable between Bottom Potence and SOLAR crate
221 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL10-O | SOL10-O-C3 | C-side | On potence side STAUBLI 10O: connector 16 pins (for 4 mm2 wires); no connector on SOLAR crate side (cable inserted in WAGO 826-164) | 1 | 0 | 4 (tbc) | N | 0 | N | N | N | cable on CH10O potence (Station 5): 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative ; cable between Bottom Potence and SOLAR crate
222 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL10-O | SOL10-O-C4 | C-side | On potence side STAUBLI 10O: connector 16 pins (for 4 mm2 wires); no connector on SOLAR crate side (cable inserted in WAGO 826-164) | 1 | 0 | 3,5 (tbc) | N | 0 | N | N | N | cable on CH10O potence (Station 5): 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative ; cable between Bottom Potence and SOLAR crate
223 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL10-O | SOL10-O-C5 | C-side | On potence side STAUBLI 10O: connector 16 pins (for 4 mm2 wires); no connector on SOLAR crate side (cable inserted in WAGO 826-164) | 1 | 0 | 3 (tbc) | N | 0 | N | N | N | cable on CH10O potence (Station 5): 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative ; cable between Bottom Potence and SOLAR crate
224 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL10-O | SOL10-IO-C6 | C-side | On potence side STAUBLI 10O: connector 16 pins (for 4 mm2 wires); no connector on SOLAR crate side (cable inserted in WAGO 826-164) | 1 | 0 | 2,5 (tbc) | N | 0 | N | N | N | cable on CH10O potence (Station 5): 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative ; cable between Bottom Potence and SOLAR crate
225 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL10-O | SOL10-O-C7 | C-side | On potence side STAUBLI 10O: connector 16 pins (for 4 mm2 wires); no connector on SOLAR crate side (cable inserted in WAGO 826-164) | 1 | 0 | 2 (tbc) | N | 0 | N | N | N | cable on CH10O potence (Station 5): 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative ; cable between Bottom Potence and SOLAR crate
226 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL10-O | SOL10-O-C8 | C-side | On potence side STAUBLI 10O: connector 16 pins (for 4 mm2 wires); no connector on SOLAR crate side (cable inserted in WAGO 826-164) | 1 | 0 | 1,5 (tbc) | N | 0 | N | N | N | cable on CH10O potence (Station 5): 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative ; cable between Bottom Potence and SOLAR crate
Sense SOLAR on potence OUTSIDE
197 | MCH | Sense (SOLAR crate) |  |  | 04.21.52.130.6 | 0.5 mm2 | SOL7-O | SOL7-O-C1 | C-side | On potence side BURNDY7O (connecteur 16 pins); no connector on SOLAR crate side (cable inserted in WAGO 826-164) | 1 | 0 | 4,5 (tbc) | N | 0 | N | N | N | cable on CH7O potence (Station 4):1 cable = 9 pairs of sense = 9x2 0.5 mm2 NE18 == 1 half-chamber station 4; length is approximative; cable between potence and SOLAR crate
198 | MCH | Sense SOLAR |  |  | 04.21.52.130.6 | 0.5 mm2 | SOL7-O | SOL7-O-C2 | C-side | On potence side BURNDY7O; no connector on SOLAR crate side | 1 | 0 | 4 (tbc) | N | 0 | N | N | N | cable on CH7O potence (Station 4):1 cable = 9 pairs of sense = 9x2 0.5 mm2 NE18 == 1 half-chamber station 4; length is approximative; cable between potence and SOLAR crate
199 | MCH | Sense SOLAR |  |  | 04.21.52.130.6 | 0.5 mm2 | SOL7-O | SOL7-O-C3 | C-side | On potence side BURNDY7O; no connector on SOLAR crate side | 1 | 0 | 3,5 (tbc) | N | 0 | N | N | N | cable on CH7O potence (Station 4):1 cable = 9 pairs of sense = 9x2 0.5 mm2 NE18 == 1 half-chamber station 4; length is approximative; cable between potence and SOLAR crate
200 | MCH | Sense SOLAR |  |  | 04.21.52.130.6 | 0.5 mm2 | SOL7-O | SOL7-O-C4 | C-side | On potence side BURNDY7O; no connector on SOLAR crate side | 1 | 0 | 3 (tbc) | N | 0 | N | N | N | cable on CH7O potence (Station 4):1 cable = 9 pairs of sense = 9x2 0.5 mm2 NE18 == 1 half-chamber station 4; length is approximative; cable between potence and SOLAR crate
201 | MCH | Sense SOLAR |  |  | 04.21.52.130.6 | 0.5 mm2 | SOL7-O | SOL7-O-C5 | C-side | On potence side BURNDY7O; no connector on SOLAR crate side | 1 | 0 | 2,5 (tbc) | N | 0 | N | N | N | cable on CH7O potence (Station 4):1 cable = 9 pairs of sense = 9x2 0.5 mm2 NE18 == 1 half-chamber station 4; length is approximative; cable between potence and SOLAR crate
202 | MCH | Sense SOLAR |  |  | 04.21.52.130.6 | 0.5 mm2 | SOL7-O | SOL7-O-C6 | C-side | On potence side BURNDY7O; no connector on SOLAR crate side | 1 | 0 | 2 (tbc) | N | 0 | N | N | N | cable on CH7O potence (Station 4):1 cable = 9 pairs of sense = 9x2 0.5 mm2 NE18 == 1 half-chamber station 4; length is approximative; cable between potence and SOLAR crate
203 | MCH | Sense SOLAR |  |  | 04.21.52.130.6 | 0.5 mm2 | SOL7-O | SOL7-O-C7 | C-side | On potence side BURNDY7O; no connector on SOLAR crate side | 1 | 0 | 1,5 (tbc) | N | 0 | N | N | N | cable on CH7O potence (Station 4):1 cable = 9 pairs of sense = 9x2 0.5 mm2 NE18 == 1 half-chamber station 4; length is approximative; cable between potence and SOLAR crate
204 | MCH | Sense SOLAR |  |  | 04.21.52.130.6 | 0.5 mm2 | SOL8-O | SOL8-O-C1 | C-side | On potence side BURNDY 8O; no connector on SOLAR crate side | 1 | 0 | 4,5 (tbc) | N | 0 | N | N | N | cable on CH8O potence (Station 4):1 cable = 9 pairs of sense = 9x2 0.5 mm2 NE18 == 1 half-chamber station 4; length is approximative; cable between potence and SOLAR crate
205 | MCH | Sense SOLAR |  |  | 04.21.52.130.6 | 0.5 mm2 | SOL8-O | SOL8-O-C2 | C-side | On potence side BURNDY 8O; no connector on SOLAR crate side | 1 | 0 | 4 (tbc) | N | 0 | N | N | N | cable on CH8O potence (Station 4):1 cable = 9 pairs of sense = 9x2 0.5 mm2 NE18 == 1 half-chamber station 4; length is approximative; cable between potence and SOLAR crate
206 | MCH | Sense SOLAR |  |  | 04.21.52.130.6 | 0.5 mm2 | SOL8-O | SOL8-O-C3 | C-side | On potence side BURNDY 8O; no connector on SOLAR crate side | 1 | 0 | 3,5 (tbc) | N | 0 | N | N | N | cable on CH8O potence (Station 4):1 cable = 9 pairs of sense = 9x2 0.5 mm2 NE18 == 1 half-chamber station 4; length is approximative; cable between potence and SOLAR crate
207 | MCH | Sense SOLAR |  |  | 04.21.52.130.6 | 0.5 mm2 | SOL8-O | SOL8-O-C4 | C-side | On potence side BURNDY 8O; no connector on SOLAR crate side | 1 | 0 | 3 (tbc) | N | 0 | N | N | N | cable on CH8O potence (Station 4):1 cable = 9 pairs of sense = 9x2 0.5 mm2 NE18 == 1 half-chamber station 4; length is approximative; cable between potence and SOLAR crate
208 | MCH | Sense SOLAR |  |  | 04.21.52.130.6 | 0.5 mm2 | SOL8-O | SOL8-O-C5 | C-side | On potence side BURNDY 8O; no connector on SOLAR crate side | 1 | 0 | 2,5 (tbc) | N | 0 | N | N | N | cable on CH8O potence (Station 4):1 cable = 9 pairs of sense = 9x2 0.5 mm2 NE18 == 1 half-chamber station 4; length is approximative; cable between potence and SOLAR crate
209 | MCH | Sense SOLAR |  |  | 04.21.52.130.6 | 0.5 mm2 | SOL8-O | SOL8-O-C6 | C-side | On potence side BURNDY 8O; no connector on SOLAR crate side | 1 | 0 | 2 (tbc) | N | 0 | N | N | N | cable on CH8O potence (Station 4):1 cable = 9 pairs of sense = 9x2 0.5 mm2 NE18 == 1 half-chamber station 4; length is approximative; cable between potence and SOLAR crate
210 | MCH | Sense SOLAR |  |  | 04.21.52.130.6 | 0.5 mm2 | SOL8-O | SOL8-O-C7 | C-side | On potence side BURNDY 8O; no connector on SOLAR crate side | 1 | 0 | 1,5 (tbc) | N | 0 | N | N | N | cable on CH8O potence (Station 4):1 cable = 9 pairs of sense = 9x2 0.5 mm2 NE18 == 1 half-chamber station 4; length is approximative; cable between potence and SOLAR crate
211 | MCH | Sense SOLAR |  |  | 04.21.52.130.6 | 0.5 mm2 | SOL9-O | SOL9-O-C1 | C-side | On potence side BURNDY 9O; no connector on SOLAR crate side | 1 | 0 | 5 (tbc) | N | 0 | N | N | N | cable on CH9O potence (Station 4):1 cable = 9 pairs of sense = 9x2 0.5 mm2 NE18 == 1 half-chamber station 4; length is approximative; cable between potence and SOLAR crate
212 | MCH | Sense SOLAR |  |  | 04.21.52.130.6 | 0.5 mm2 | SOL9-O | SOL9-O-C2 | C-side | On potence side BURNDY 9O; no connector on SOLAR crate side | 1 | 0 | 4,5 (tbc) | N | 0 | N | N | N | cable on CH9O potence (Station 4):1 cable = 9 pairs of sense = 9x2 0.5 mm2 NE18 == 1 half-chamber station 4; length is approximative; cable between potence and SOLAR crate
213 | MCH | Sense SOLAR |  |  | 04.21.52.130.6 | 0.5 mm2 | SOL9-O | SOL9-O-C3 | C-side | On potence side BURNDY 9O; no connector on SOLAR crate side | 1 | 0 | 4 (tbc) | N | 0 | N | N | N | cable on CH9O potence (Station 4):1 cable = 9 pairs of sense = 9x2 0.5 mm2 NE18 == 1 half-chamber station 4; length is approximative; cable between potence and SOLAR crate
214 | MCH | Sense SOLAR |  |  | 04.21.52.130.6 | 0.5 mm2 | SOL9-O | SOL9-O-C4 | C-side | On potence side BURNDY 9O; no connector on SOLAR crate side | 1 | 0 | 3,5 (tbc) | N | 0 | N | N | N | cable on CH9O potence (Station 4):1 cable = 9 pairs of sense = 9x2 0.5 mm2 NE18 == 1 half-chamber station 4; length is approximative; cable between potence and SOLAR crate
215 | MCH | Sense SOLAR |  |  | 04.21.52.130.6 | 0.5 mm2 | SOL9-O | SOL9-O-C5 | C-side | On potence side BURNDY 9O; no connector on SOLAR crate side | 1 | 0 | 3 (tbc) | N | 0 | N | N | N | cable on CH9O potence (Station 4):1 cable = 9 pairs of sense = 9x2 0.5 mm2 NE18 == 1 half-chamber station 4; length is approximative; cable between potence and SOLAR crate
216 | MCH | Sense SOLAR |  |  | 04.21.52.130.6 | 0.5 mm2 | SOL9-O | SOL9-O-C6 | C-side | On potence side BURNDY 9O; no connector on SOLAR crate side | 1 | 0 | 2,5 (tbc) | N | 0 | N | N | N | cable on CH9O potence (Station 4):1 cable = 9 pairs of sense = 9x2 0.5 mm2 NE18 == 1 half-chamber station 4; length is approximative; cable between potence and SOLAR crate
217 | MCH | Sense SOLAR |  |  | 04.21.52.130.6 | 0.5 mm2 | SOL9-O | SOL9-O-C7 | C-side | On potence side BURNDY 9O; no connector on SOLAR crate side | 1 | 0 | 2 (tbc) | N | 0 | N | N | N | cable on CH9O potence (Station 4):1 cable = 9 pairs of sense = 9x2 0.5 mm2 NE18 == 1 half-chamber station 4; length is approximative; cable between potence and SOLAR crate
218 | MCH | Sense SOLAR |  |  | 04.21.52.130.6 | 0.5 mm2 | SOL9-O | SOL9-O-C8 | C-side | On potence side BURNDY 9O; no connector on SOLAR crate side | 1 | 0 | 1,5 (tbc) | N | 0 | N | N | N | cable on CH9O potence (Station 4):1 cable = 9 pairs of sense = 9x2 0.5 mm2 NE18 == 1 half-chamber station 4; length is approximative; cable between potence and SOLAR crate
219 | MCH | Sense SOLAR |  |  | 04.21.52.130.6 | 0.5 mm2 | SOL10-O | SOL10-O-C1 | C-side | On potence side BURNDY 10O; no connector on SOLAR crate side | 1 | 0 | 5 (tbc) | N | 0 | N | N | N | cable on CH10O potence (Station 4):1 cable = 9 pairs of sense = 9x2 0.5 mm2 NE18 == 1 half-chamber station 4; length is approximative; cable between potence and SOLAR crate
220 | MCH | Sense SOLAR |  |  | 04.21.52.130.6 | 0.5 mm2 | SOL10-O | SOL10-O-C2 | C-side | On potence side BURNDY 10O; no connector on SOLAR crate side | 1 | 0 | 4,5 (tbc) | N | 0 | N | N | N | cable on CH10O potence (Station 4):1 cable = 9 pairs of sense = 9x2 0.5 mm2 NE18 == 1 half-chamber station 4; length is approximative; cable between potence and SOLAR crate
221 | MCH | Sense SOLAR |  |  | 04.21.52.130.6 | 0.5 mm2 | SOL10-O | SOL10-O-C3 | C-side | On potence side BURNDY 10O; no connector on SOLAR crate side | 1 | 0 | 4 (tbc) | N | 0 | N | N | N | cable on CH10O potence (Station 4):1 cable = 9 pairs of sense = 9x2 0.5 mm2 NE18 == 1 half-chamber station 4; length is approximative; cable between potence and SOLAR crate
222 | MCH | Sense SOLAR |  |  | 04.21.52.130.6 | 0.5 mm2 | SOL10-O | SOL10-O-C4 | C-side | On potence side BURNDY 10O; no connector on SOLAR crate side | 1 | 0 | 3,5 (tbc) | N | 0 | N | N | N | cable on CH10O potence (Station 4):1 cable = 9 pairs of sense = 9x2 0.5 mm2 NE18 == 1 half-chamber station 4; length is approximative; cable between potence and SOLAR crate
223 | MCH | Sense SOLAR |  |  | 04.21.52.130.6 | 0.5 mm2 | SOL10-O | SOL10-O-C5 | C-side | On potence side BURNDY 10O; no connector on SOLAR crate side | 1 | 0 | 3 (tbc) | N | 0 | N | N | N | cable on CH10O potence (Station 4):1 cable = 9 pairs of sense = 9x2 0.5 mm2 NE18 == 1 half-chamber station 4; length is approximative; cable between potence and SOLAR crate
224 | MCH | Sense SOLAR |  |  | 04.21.52.130.6 | 0.5 mm2 | SOL10-O | SOL10-IO-C6 | C-side | On potence side BURNDY 10O; no connector on SOLAR crate side | 1 | 0 | 2,5 (tbc) | N | 0 | N | N | N | cable on CH10O potence (Station 4):1 cable = 9 pairs of sense = 9x2 0.5 mm2 NE18 == 1 half-chamber station 4; length is approximative; cable between potence and SOLAR crate
225 | MCH | Sense SOLAR |  |  | 04.21.52.130.6 | 0.5 mm2 | SOL10-O | SOL10-O-C7 | C-side | On potence side BURNDY 10O; no connector on SOLAR crate side | 1 | 0 | 2 (tbc) | N | 0 | N | N | N | cable on CH10O potence (Station 4):1 cable = 9 pairs of sense = 9x2 0.5 mm2 NE18 == 1 half-chamber station 4; length is approximative; cable between potence and SOLAR crate
226 | MCH | Sense SOLAR |  |  | 04.21.52.130.6 | 0.5 mm2 | SOL10-O | SOL10-O-C8 | C-side | On potence side BURNDY 10O; no connector on SOLAR crate side | 1 | 0 | 1,5 (tbc) | N | 0 | N | N | N | cable on CH10O potence (Station 4):1 cable = 9 pairs of sense = 9x2 0.5 mm2 NE18 == 1 half-chamber station 4; length is approximative; cable between potence and SOLAR crate
LV SOLAR INISDE
55 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 (4 mm2) | SOL1-I-C1 | SOLC08-1-1 | C-side | Bended lug M6 on LVPS side; no connector on SOLAR crate side (cable inserted in WAGO 826-164) | 1 | 0 | 25 (tbc) | N | 0 | N | N | N | 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative; cable between LVPS and SOLAR crate
56 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL1-I-C2 | SOLC08-1-2 | C-side | Bended lug M6 on LVPS side; no connector on SOLAR crate side | 1 | 0 | 25 (tbc) | N | 0 | N | N | N | 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative; cable between LVPS and SOLAR crate
57 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL1-I-C3 | SOLC08-1-3 | C-side | Bended lug M6 on LVPS side; no connector on SOLAR crate side | 1 | 0 | 25 (tbc) | N | 0 | N | N | N | 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative; cable between LVPS and SOLAR crate
58 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL1-I-C4 | SOLC08-1-4 | C-side | Bended lug M6 on LVPS side; no connector on SOLAR crate side | 1 | 0 | 25 (tbc) | N | 0 | N | N | N | 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative; cable between LVPS and SOLAR crate
59 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL2-I-C1 | SOLC08-1-5 | C-side | Bended lug M6 on LVPS side; no connector on SOLAR crate side | 1 | 0 | 25 (tbc) | N | 0 | N | N | N | 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative; cable between LVPS and SOLAR crate
60 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL2-I-C2 | SOLC08-1-6 | C-side | Bended lug M6 on LVPS side; no connector on SOLAR crate side | 1 | 0 | 25 (tbc) | N | 0 | N | N | N | 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative; cable between LVPS and SOLAR crate
61 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL2-I-C3 | SOLC08-1-7 | C-side | Bended lug M6 on LVPS side; no connector on SOLAR crate side | 1 | 0 | 25 (tbc) | N | 0 | N | N | N | 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative; cable between LVPS and SOLAR crate
62 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL2-I-C4 | SOLC08-1-8 | C-side | Bended lug M6 on LVPS side; no connector on SOLAR crate side | 1 | 0 | 25 (tbc) | N | 0 | N | N | N | 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative; cable between LVPS and SOLAR crate
63 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL3-I-C1 | SOLC08-2-1 | C-side | Bended lug M6 on LVPS side; no connector on SOLAR crate side | 1 | 0 | 25 (tbc) | N | 0 | N | N | N | 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative; cable between LVPS and SOLAR crate
64 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL3-I-C2 | SOLC08-2-2 | C-side | Bended lug M6 on LVPS side; no connector on SOLAR crate side | 1 | 0 | 25 (tbc) | N | 0 | N | N | N | 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative; cable between LVPS and SOLAR crate
65 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL3-I-C3 | SOLC08-2-3 | C-side | Bended lug M6 on LVPS side; no connector on SOLAR crate side | 1 | 0 | 25 (tbc) | N | 0 | N | N | N | 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative; cable between LVPS and SOLAR crate
66 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL3-I-C4 | SOLC08-2-4 | C-side | Bended lug M6 on LVPS side; no connector on SOLAR crate side | 1 | 0 | 25 (tbc) | N | 0 | N | N | N | 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative; cable between LVPS and SOLAR crate
67 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL4-I-C1 | SOLC08-2-5 | C-side | Bended lug M6 on LVPS side; no connector on SOLAR crate side | 1 | 0 | 25 (tbc) | N | 0 | N | N | N | 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative; cable between LVPS and SOLAR crate
68 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL4-I-C2 | SOLC08-2-6 | C-side | Bended lug M6 on LVPS side; no connector on SOLAR crate side | 1 | 0 | 25 (tbc) | N | 0 | N | N | N | 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative; cable between LVPS and SOLAR crate
69 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL4-I-C3 | SOLC08-2-7 | C-side | Bended lug M6 on LVPS side; no connector on SOLAR crate side | 1 | 0 | 25 (tbc) | N | 0 | N | N | N | 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative; cable between LVPS and SOLAR crate
70 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL4-I-C4 | SOLC08-2-8 | C-side | Bended lug M6 on LVPS side; no connector on SOLAR crate side | 1 | 0 | 25 (tbc) | N | 0 | N | N | N | 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative; cable between LVPS and SOLAR crate
71 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL5-I-C1 | SOLC08-3-1 | C-side | Bended lug M6 on LVPS side; no connector on SOLAR crate side | 1 | 0 | 20 (tbc) | N | 0 | N | N | N | 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative; cable between LVPS and SOLAR crate
72 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL5-I-C2 | SOLC08-3-2 | C-side | Bended lug M6 on LVPS side; no connector on SOLAR crate side | 1 | 0 | 20 (tbc) | N | 0 | N | N | N | 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative; cable between LVPS and SOLAR crate
73 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL5-I-C3 | SOLC08-3-3 | C-side | Bended lug M6 on LVPS side; no connector on SOLAR crate side | 1 | 0 | 20 (tbc) | N | 0 | N | N | N | 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative; cable between LVPS and SOLAR crate
74 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL5-I-C4 | SOLC08-3-4 | C-side | Bended lug M6 on LVPS side; no connector on SOLAR crate side | 1 | 0 | 20 (tbc) | N | 0 | N | N | N | 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative; cable between LVPS and SOLAR crate
161 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL5-I-C5 | SOLC36-3-5 | C-side | Bended lug M6 on LVPS side; no connector on SOLAR crate side | 1 | 0 | 20 (tbc) | N | 0 | N | N | N | 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative; cable between LVPS and SOLAR crate
162 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL6-I-C1 | SOLC36-3-6 | C-side | Bended lug M6 on LVPS side; no connector on SOLAR crate side | 1 | 0 | 20 (tbc) | N | 0 | N | N | N | 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative; cable between LVPS and SOLAR crate
163 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL6-I-C2 | SOLC36-3-7 | C-side | Bended lug M6 on LVPS side; no connector on SOLAR crate side | 1 | 0 | 20 (tbc) | N | 0 | N | N | N | 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative; cable between LVPS and SOLAR crate
164 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL6-I-C3 | SOLC36-3-8 | C-side | Bended lug M6 on LVPS side; no connector on SOLAR crate side | 1 | 0 | 20 (tbc) | N | 0 | N | N | N | 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative; cable between LVPS and SOLAR crate
165 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL6-I-C4 | SOLC36-3-9 | C-side | Bended lug M6 on LVPS side; no connector on SOLAR crate side | 1 | 0 | 20 (tbc) | N | 0 | N | N | N | 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative; cable between LVPS and SOLAR crate
166 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL6-I-C5 | SOLC36-3-10 | C-side | Bended lug M6 on LVPS side; no connector on SOLAR crate side |  | 0 | 20 (tbc) | N | 0 | N | N | N | 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative; cable between LVPS and SOLAR crate
167 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL7-I | SOLC36-4-1 | C-side | Bended lug M6 on LVPS side; On potence side STAUBLI 7I | 1 | 0 | 15 (tbc) | N | 0 | N | N | N | 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative; cable between LVPS and potence
168 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL7-I | SOLC36-4-2 | C-side | Bended lug M6 on LVPS side; On potence side STAUBLI 7I | 1 | 0 | 15 (tbc) | N | 0 | N | N | N | 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative; cable between LVPS and potence
169 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL7-I | SOLC36-4-3 | C-side | Bended lug M6 on LVPS side; On potence side STAUBLI 7I | 1 | 0 | 15 (tbc) | N | 0 | N | N | N | 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative; cable between LVPS and potence
170 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL7-I | SOLC36-4-4 | C-side | Bended lug M6 on LVPS side; On potence side STAUBLI 7I | 1 | 0 | 15 (tbc) | N | 0 | N | N | N | 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative; cable between LVPS and potence
171 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL7-I | SOLC36-4-5 | C-side | Bended lug M6 on LVPS side; On potence side STAUBLI 7I | 1 | 0 | 15 (tbc) | N | 0 | N | N | N | 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative; cable between LVPS and potence
172 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL7-I | SOLC36-4-6 | C-side | Bended lug M6 on LVPS side; On potence side STAUBLI 7I | 1 | 0 | 15 (tbc) | N | 0 | N | N | N | 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative; cable between LVPS and potence
173 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL7-I | SOLC36-4-7 | C-side | Bended lug M6 on LVPS side; On potence side STAUBLI 7I | 1 | 0 | 15 (tbc) | N | 0 | N | N | N | 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative; cable between LVPS and potence
174 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL8-I | SOLC36-4-8 | C-side | Bended lug M6 on LVPS side; On potence side STAUBLI 8I | 1 | 0 | 15 (tbc) | N | 0 | N | N | N | 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative; cable between LVPS and potence
175 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL8-I | SOLC36-4-9 | C-side | Bended lug M6 on LVPS side; On potence side STAUBLI 8I | 1 | 0 | 15 (tbc) | N | 0 | N | N | N | 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative; cable between LVPS and potence
176 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL8-I | SOLC36-4-10 | C-side | Bended lug M6 on LVPS side; On potence side STAUBLI 8I | 1 | 0 | 15 (tbc) | N | 0 | N | N | N | 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative; cable between LVPS and potence
177 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL8-I | SOLC36-4-11 | C-side | Bended lug M6 on LVPS side; On potence side STAUBLI 8I | 1 | 0 | 15 (tbc) | N | 0 | N | N | N | 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative; cable between LVPS and potence
178 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL8-I | SOLC36-4-12 | C-side | Bended lug M6 on LVPS side; On potence side STAUBLI 8I | 1 | 0 | 15 (tbc) | N | 0 | N | N | N | 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative; cable between LVPS and potence
179 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL8-I | SOLC36-5-1 | C-side | Bended lug M6 on LVPS side; On potence side STAUBLI 8I | 1 | 0 | 15 (tbc) | N | 0 | N | N | N | 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative; cable between LVPS and potence
180 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL8-I | SOLC36-5-2 | C-side | Bended lug M6 on LVPS side; On potence side STAUBLI 8I | 1 | 0 | 15 (tbc) | N | 0 | N | N | N | 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative; cable between LVPS and potence
181 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL9-I | SOLC36-5-3 | C-side | Bended lug M6 on LVPS side; On potence side STAUBLI 9I | 1 | 0 | 15 (tbc) | N | 0 | N | N | N | 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative; cable between LVPS and potence
182 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL9-I | SOLC36-5-4 | C-side | Bended lug M6 on LVPS side; On potence side STAUBLI 9I | 1 | 0 | 15 (tbc) | N | 0 | N | N | N | 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative; cable between LVPS and potence
183 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL9-I | SOLC36-5-5 | C-side | Bended lug M6 on LVPS side; On potence side STAUBLI 9I | 1 | 0 | 15 (tbc) | N | 0 | N | N | N | 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative; cable between LVPS and potence
184 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL9-I | SOLC36-5-6 | C-side | Bended lug M6 on LVPS side; On potence side STAUBLI 9I | 1 | 0 | 15 (tbc) | N | 0 | N | N | N | 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative; cable between LVPS and potence
185 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL9-I | SOLC36-5-7 | C-side | Bended lug M6 on LVPS side; On potence side STAUBLI 9I | 1 | 0 | 15 (tbc) | N | 0 | N | N | N | 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative; cable between LVPS and potence
186 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL9-I | SOLC36-5-8 | C-side | Bended lug M6 on LVPS side; On potence side STAUBLI 9I | 1 | 0 | 15 (tbc) | N | 0 | N | N | N | 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative; cable between LVPS and potence
187 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL9-I | SOLC36-5-9 | C-side | Bended lug M6 on LVPS side; On potence side STAUBLI 9I | 1 | 0 | 15 (tbc) | N | 0 | N | N | N | 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative; cable between LVPS and potence
188 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL9-I | SOLC36-5-10 | C-side | Bended lug M6 on LVPS side; On potence side STAUBLI 9I | 1 | 0 | 15 (tbc) | N | 0 | N | N | N | 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative; cable between LVPS and potence
189 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL10-I | SOLC36-6-1 | C-side | Bended lug M6 on LVPS side; On potence side STAUBLI 10I | 1 | 0 | 15 (tbc) | N | 0 | N | N | N | 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative; cable between LVPS and potence
190 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL10-I | SOLC36-6-2 | C-side | Bended lug M6 on LVPS side; On potence side STAUBLI 10I | 1 | 0 | 15 (tbc) | N | 0 | N | N | N | 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative; cable between LVPS and potence
191 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL10-I | SOLC36-6-3 | C-side | Bended lug M6 on LVPS side; On potence side STAUBLI 10I | 1 | 0 | 15 (tbc) | N | 0 | N | N | N | 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative; cable between LVPS and potence
192 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL10-I | SOLC36-6-4 | C-side | Bended lug M6 on LVPS side; On potence side STAUBLI 10I | 1 | 0 | 15 (tbc) | N | 0 | N | N | N | 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative; cable between LVPS and potence
193 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL10-I | SOLC36-6-5 | C-side | Bended lug M6 on LVPS side; On potence side STAUBLI 10I | 1 | 0 | 15 (tbc) | N | 0 | N | N | N | 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative; cable between LVPS and potence
194 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL10-I | SOLC36-6-6 | C-side | Bended lug M6 on LVPS side; On potence side STAUBLI 10I | 1 | 0 | 15 (tbc) | N | 0 | N | N | N | 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative; cable between LVPS and potence
195 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL10-I | SOLC36-6-7 | C-side | Bended lug M6 on LVPS side; On potence side STAUBLI 10I | 1 | 0 | 15 (tbc) | N | 0 | N | N | N | 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative; cable between LVPS and potence
196 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL10-I | SOLC36-6-8 | C-side | Bended lug M6 on LVPS side; On potence side STAUBLI 10I | 1 | 0 | 15 (tbc) | N | 0 | N | N | N | 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative; cable between LVPS and potence
Sense SOLAR INSDE
55 | MCH | Sense (SOLAR crates) |  |  | 04.21.52.104.0 (NE4) | 0.5 mm2 | SOL1-I-C1 | SOLC36-1-1 | C-side | No connector on LVPS side (cable inserted in LVPS sense connector); no connector on SOLAR crate side (cable inserted in WAGO 826-164) | 1 | 0 | 25 (tbc) | N | 0 | N | N | N | 1 cable = 2 pairs of sense = 2x2 0.5 mm2 NE4 == 1 quadrant; length is approximative; cable between LVPS and SOLAR crate
56 | MCH | Sense SOLAR |  |  | 04.21.52.104.0 | 0.5 mm2 | SOL1-I-C2 | SOLC36-1-2 | C-side | No connector on LVPS side (cable inserted in LVPS sense connector); no connector on SOLAR crate side (cable inserted in WAGO 826-164) | 1 | 0 | 25 (tbc) | N | 0 | N | N | N | 1 cable = 2 pairs of sense = 2x2 0.5 mm2 NE4 == 1 quadrant; length is approximative; cable between LVPS and SOLAR crate
57 | MCH | Sense SOLAR |  |  | 04.21.52.104.0 | 0.5 mm2 | SOL1-I-C3 | SOLC36-1-3 | C-side | No connector on LVPS side (cable inserted in LVPS sense connector); no connector on SOLAR crate side (cable inserted in WAGO 826-164) | 1 | 0 | 25 (tbc) | N | 0 | N | N | N | 1 cable = 2 pairs of sense = 4x0.5 mm2 NE4 == 1 quadrant; length is approximative; cable between LVPS and SOLAR crate
58 | MCH | Sense SOLAR |  |  | 04.21.52.104.0 | 0.5 mm2 | SOL1-I-C4 | SOLC36-1-4 | C-side | No connector on LVPS side (cable inserted in LVPS sense connector); no connector on SOLAR crate side (cable inserted in WAGO 826-164) | 1 | 0 | 25 (tbc) | N | 0 | N | N | N | 1 cable = 2 pairs of sense = 2x2 0.5 mm2 NE4 == 1 quadrant; length is approximative; cable between LVPS and SOLAR crate
59 | MCH | Sense SOLAR |  |  | 04.21.52.104.0 | 0.5 mm2 | SOL2-I-C1 | SOLC36-1-5 | C-side | No connector on LVPS side (cable inserted in LVPS sense connector); no connector on SOLAR crate side (cable inserted in WAGO 826-164) | 1 | 0 | 25 (tbc) | N | 0 | N | N | N | 1 cable = 2 pairs of sense = 2x2 0.5 mm2 NE4 == 1 quadrant; length is approximative; cable between LVPS and SOLAR crate
60 | MCH | Sense SOLAR |  |  | 04.21.52.104.0 | 0.5 mm2 | SOL2-I-C2 | SOLC36-1-6 | C-side | No connector on LVPS side (cable inserted in LVPS sense connector); no connector on SOLAR crate side (cable inserted in WAGO 826-164) | 1 | 0 | 25 (tbc) | N | 0 | N | N | N | 1 cable = 2 pairs of sense = 2x2 0.5 mm2 NE4 == 1 quadrant; length is approximative; cable between LVPS and SOLAR crate
61 | MCH | Sense SOLAR |  |  | 04.21.52.104.0 | 0.5 mm2 | SOL2-I-C3 | SOLC36-1-7 | C-side | No connector on LVPS side (cable inserted in LVPS sense connector); no connector on SOLAR crate side (cable inserted in WAGO 826-164) | 1 | 0 | 25 (tbc) | N | 0 | N | N | N | 1 cable = 2 pairs of sense = 2x2 0.5 mm2 NE4 == 1 quadrant; length is approximative; cable between LVPS and SOLAR crate
62 | MCH | Sense SOLAR |  |  | 04.21.52.104.0 | 0.5 mm2 | SOL2-I-C4 | SOLC36-1-8 | C-side | No connector on LVPS side (cable inserted in LVPS sense connector); no connector on SOLAR crate side (cable inserted in WAGO 826-164) | 1 | 0 | 25 (tbc) | N | 0 | N | N | N | 1 cable = 2 pairs of sense = 2x2 0.5 mm2 NE4 == 1 quadrant; length is approximative; cable between LVPS and SOLAR crate
63 | MCH | Sense SOLAR |  |  | 04.21.52.104.0 | 0.5 mm2 | SOL3-I-C1 | SOLC36-2-1 | C-side | No connector on LVPS side (cable inserted in LVPS sense connector); no connector on SOLAR crate side (cable inserted in WAGO 826-164) | 1 | 0 | 25 (tbc) | N | 0 | N | N | N | 1 cable = 2 pairs of sense = 2x2 0.5 mm2 NE4 == 1 quadrant; length is approximative; cable between LVPS and SOLAR crate
64 | MCH | Sense SOLAR |  |  | 04.21.52.104.0 | 0.5 mm2 | SOL3-I-C2 | SOLC36-2-2 | C-side | No connector on LVPS side (cable inserted in LVPS sense connector); no connector on SOLAR crate side (cable inserted in WAGO 826-164) | 1 | 0 | 25 (tbc) | N | 0 | N | N | N | 1 cable = 2 pairs of sense = 2x2 0.5 mm2 NE4 == 1 quadrant; length is approximative; cable between LVPS and SOLAR crate
65 | MCH | Sense SOLAR |  |  | 04.21.52.104.0 | 0.5 mm2 | SOL3-I-C3 | SOLC36-2-3 | C-side | No connector on LVPS side (cable inserted in LVPS sense connector); no connector on SOLAR crate side (cable inserted in WAGO 826-164) | 1 | 0 | 25 (tbc) | N | 0 | N | N | N | 1 cable = 2 pairs of sense = 2x2 0.5 mm2 NE4 == 1 quadrant; length is approximative; cable between LVPS and SOLAR crate
66 | MCH | Sense SOLAR |  |  | 04.21.52.104.0 | 0.5 mm2 | SOL3-I-C4 | SOLC36-2-4 | C-side | No connector on LVPS side (cable inserted in LVPS sense connector); no connector on SOLAR crate side (cable inserted in WAGO 826-164) | 1 | 0 | 25 (tbc) | N | 0 | N | N | N | 1 cable = 2 pairs of sense = 2x2 0.5 mm2 NE4 == 1 quadrant; length is approximative; cable between LVPS and SOLAR crate
67 | MCH | Sense SOLAR |  |  | 04.21.52.104.0 | 0.5 mm2 | SOL4-I-C1 | SOLC36-2-5 | C-side | No connector on LVPS side (cable inserted in LVPS sense connector); no connector on SOLAR crate side (cable inserted in WAGO 826-164) | 1 | 0 | 25 (tbc) | N | 0 | N | N | N | 1 cable = 2 pairs of sense = 2x2 0.5 mm2 NE4 == 1 quadrant; length is approximative; cable between LVPS and SOLAR crate
68 | MCH | Sense SOLAR |  |  | 04.21.52.104.0 | 0.5 mm2 | SOL4-I-C2 | SOLC36-2-6 | C-side | No connector on LVPS side (cable inserted in LVPS sense connector); no connector on SOLAR crate side (cable inserted in WAGO 826-164) | 1 | 0 | 25 (tbc) | N | 0 | N | N | N | 1 cable = 2 pairs of sense = 2x2 0.5 mm2 NE4 == 1 quadrant; length is approximative; cable between LVPS and SOLAR crate
69 | MCH | Sense SOLAR |  |  | 04.21.52.104.0 | 0.5 mm2 | SOL4-I-C3 | SOLC36-2-7 | C-side | No connector on LVPS side (cable inserted in LVPS sense connector); no connector on SOLAR crate side (cable inserted in WAGO 826-164) | 1 | 0 | 25 (tbc) | N | 0 | N | N | N | 1 cable = 2 pairs of sense = 2x2 0.5 mm2 NE4 == 1 quadrant; length is approximative; cable between LVPS and SOLAR crate
70 | MCH | Sense SOLAR |  |  | 04.21.52.104.0 | 0.5 mm2 | SOL4-I-C4 | SOLC36-2-8 | C-side | No connector on LVPS side (cable inserted in LVPS sense connector); no connector on SOLAR crate side (cable inserted in WAGO 826-164) | 1 | 0 | 25 (tbc) | N | 0 | N | N | N | 1 cable = 2 pairs of sense = 2x2 0.5 mm2 NE4 == 1 quadrant; length is approximative; cable between LVPS and SOLAR crate
71 | MCH | Sense SOLAR |  |  | 04.21.52.120.8 (NE10) | 0.5 mm2 | SOL5-I-C1 | SOLC36-3-1 | C-side | No connector on LVPS side (cable inserted in LVPS sense connector); no connector on SOLAR crate side (cable inserted in WAGO 826-164) | 1 | 0 | 20 (tbc) | N | 0 | N | N | N | 1 cable = 5 pairs of sense = 5x2 0.5 mm2 NE10 == 1 half-chamber station 3; length is approximative; cable between LVPS and SOLAR crate
72 | MCH | Sense SOLAR |  |  | 04.21.52.120.8 (NE10) | 0.5 mm2 | SOL5-OI-C2 | SOLC36-3-2 | C-side | No connector on LVPS side (cable inserted in LVPS sense connector); no connector on SOLAR crate side (cable inserted in WAGO 826-164) | 1 | 0 | 20 (tbc) | N | 0 | N | N | N | 1 cable = 5 pairs of sense = 5x2 0.5 mm2 NE10 == 1 half-chamber station 3; length is approximative; cable between LVPS and SOLAR crate
73 | MCH | Sense SOLAR |  |  | 04.21.52.120.8 (NE10) | 0.5 mm2 | SOL5-I-C3 | SOLC36-3-3 | C-side | No connector on LVPS side (cable inserted in LVPS sense connector); no connector on SOLAR crate side (cable inserted in WAGO 826-164) | 1 | 0 | 20 (tbc) | N | 0 | N | N | N | 1 cable = 5 pairs of sense = 5x2 0.5 mm2 NE10 == 1 half-chamber station 3; length is approximative; cable between LVPS and SOLAR crate
74 | MCH | Sense SOLAR |  |  | 04.21.52.120.8 (NE10) | 0.5 mm2 | SOL5-I-C4 | SOLC36-3-4 | C-side | No connector on LVPS side (cable inserted in LVPS sense connector); no connector on SOLAR crate side (cable inserted in WAGO 826-164) | 1 | 0 | 20 (tbc) | N | 0 | N | N | N | 1 cable = 5 pairs of sense = 5x2 0.5 mm2 NE10 == 1 half-chamber station 3; length is approximative; cable between LVPS and SOLAR crate
75 | MCH | Sense SOLAR |  |  | 04.21.52.120.8 (NE10) | 0.5 mm2 | SOL5-I-C5 | SOLC36-3-5 | C-side | No connector on LVPS side (cable inserted in LVPS sense connector); no connector on SOLAR crate side (cable inserted in WAGO 826-164) | 1 | 0 | 20 (tbc) | N | 0 | N | N | N | 1 cable = 5 pairs of sense = 5x2 0.5 mm2 NE10 == 1 half-chamber station 3; length is approximative; cable between LVPS and SOLAR crate
76 | MCH | Sense SOLAR |  |  | 04.21.52.120.8 (NE10) | 0.5 mm2 | SOL6-I-C1 | SOLC36-3-6 | C-side | No connector on LVPS side (cable inserted in LVPS sense connector); no connector on SOLAR crate side (cable inserted in WAGO 826-164) | 1 | 0 | 20 (tbc) | N | 0 | N | N | N | 1 cable = 5 pairs of sense = 5x2 0.5 mm2 NE10 == 1 half-chamber station 3; length is approximative; cable between LVPS and SOLAR crate
77 | MCH | Sense SOLAR |  |  | 04.21.52.120.8 (NE10) | 0.5 mm2 | SOL6-I-C2 | SOLC36-3-7 | C-side | No connector on LVPS side (cable inserted in LVPS sense connector); no connector on SOLAR crate side (cable inserted in WAGO 826-164) | 1 | 0 | 20 (tbc) | N | 0 | N | N | N | 1 cable = 5 pairs of sense = 5x2 0.5 mm2 NE10 == 1 half-chamber station 3; length is approximative; cable between LVPS and SOLAR crate
78 | MCH | Sense SOLAR |  |  | 04.21.52.120.8 (NE10) | 0.5 mm2 | SOL6-I-C3 | SOLC36-3-8 | C-side | No connector on LVPS side (cable inserted in LVPS sense connector); no connector on SOLAR crate side (cable inserted in WAGO 826-164) | 1 | 0 | 20 (tbc) | N | 0 | N | N | N | 1 cable = 5 pairs of sense = 5x2 0.5 mm2 NE10 == 1 half-chamber station 3; length is approximative; cable between LVPS and SOLAR crate
79 | MCH | Sense SOLAR |  |  | 04.21.52.120.8 (NE10) | 0.5 mm2 | SOL6-I-C4 | SOLC36-3-9 | C-side | No connector on LVPS side (cable inserted in LVPS sense connector); no connector on SOLAR crate side (cable inserted in WAGO 826-164) | 1 | 0 | 20 (tbc) | N | 0 | N | N | N | 1 cable = 5 pairs of sense = 5x2 0.5 mm2 NE10 == 1 half-chamber station 3; length is approximative; cable between LVPS and SOLAR crate
80 | MCH | Sense SOLAR |  |  | 04.21.52.120.8 (NE10) | 0.5 mm2 | SOL6-I-C5 | SOLC36-3-10 | C-side | No connector on LVPS side (cable inserted in LVPS sense connector); no connector on SOLAR crate side (cable inserted in WAGO 826-164) |  | 0 | 20 (tbc) | N | 0 | N | N | N | 1 cable = 5 pairs of sense = 5x2 0.5 mm2 NE10 == 1 half-chamber station 3; length is approximative; cable between LVPS and SOLAR crate
81 | MCH | Sense SOLAR |  |  | 04.21.52.130.6 (NE18) | 0.5 mm2 | SOL7-I | SOLC36-4-1 | C-side | No connector on LVPS side (cable inserted in LVPS sense connector); BURNDY on potence side 7I | 1 | 0 | 15 (tbc) | N | 0 | N | N | N | 1 cable = 9 pairs of sense = 9x2 0.5 mm2 NE18 == 1 half-chamber station 4; length is approximative; cable between LVPS and potence
82 | MCH | Sense SOLAR |  |  | 04.21.52.130.6 | 0.5 mm2 | SOL7-I | SOLC36-4-2 | C-side | No connector on LVPS side (cable inserted in LVPS sense connector); BURNDY on potence side 7I | 1 | 0 | 15 (tbc) | N | 0 | N | N | N | 1 cable = 9 pairs of sense = 9x2 0.5 mm2 NE18 == 1 half-chamber station 4; length is approximative; cable between LVPS and potence
83 | MCH | Sense SOLAR |  |  | 04.21.52.130.6 | 0.5 mm2 | SOL7-I | SOLC36-4-3 | C-side | No connector on LVPS side (cable inserted in LVPS sense connector); BURNDY on potence side 7I | 1 | 0 | 15 (tbc) | N | 0 | N | N | N | 1 cable = 9 pairs of sense = 9x2 0.5 mm2 NE18 == 1 half-chamber station 4; length is approximative; cable between LVPS and potence
84 | MCH | Sense SOLAR |  |  | 04.21.52.130.6 | 0.5 mm2 | SOL7-I | SOLC36-4-4 | C-side | No connector on LVPS side (cable inserted in LVPS sense connector); BURNDY on potence side 7I | 1 | 0 | 15 (tbc) | N | 0 | N | N | N | 1 cable = 9 pairs of sense = 9x2 0.5 mm2 NE18 == 1 half-chamber station 4; length is approximative; cable between LVPS and potence
85 | MCH | Sense SOLAR |  |  | 04.21.52.130.6 | 0.5 mm2 | SOL7-I | SOLC36-4-5 | C-side | No connector on LVPS side (cable inserted in LVPS sense connector); BURNDY on potence side 7I | 1 | 0 | 15 (tbc) | N | 0 | N | N | N | 1 cable = 9 pairs of sense = 9x2 0.5 mm2 NE18 == 1 half-chamber station 4; length is approximative; cable between LVPS and potence
86 | MCH | Sense SOLAR |  |  | 04.21.52.130.6 | 0.5 mm2 | SOL7-I | SOLC36-4-6 | C-side | No connector on LVPS side (cable inserted in LVPS sense connector); BURNDY on potence side 7I | 1 | 0 | 15 (tbc) | N | 0 | N | N | N | 1 cable = 9 pairs of sense = 9x2 0.5 mm2 NE18 == 1 half-chamber station 4; length is approximative; cable between LVPS and potence
87 | MCH | Sense SOLAR |  |  | 04.21.52.130.6 | 0.5 mm2 | SOL7-I | SOLC36-4-7 | C-side | No connector on LVPS side (cable inserted in LVPS sense connector); BURNDY on potence side 7I | 1 | 0 | 15 (tbc) | N | 0 | N | N | N | 1 cable = 9 pairs of sense = 9x2 0.5 mm2 NE18 == 1 half-chamber station 4; length is approximative; cable between LVPS and potence
88 | MCH | Sense SOLAR |  |  | 04.21.52.130.6 | 0.5 mm2 | SOL8-I | SOLC36-4-8 | C-side | No connector on LVPS side (cable inserted in LVPS sense connector); BURNDY on potence side 7I | 1 | 0 | 15 (tbc) | N | 0 | N | N | N | 1 cable = 9 pairs of sense = 9x2 0.5 mm2 NE18 == 1 half-chamber station 4; length is approximative; cable between LVPS and potence
89 | MCH | Sense SOLAR |  |  | 04.21.52.130.6 | 0.5 mm2 | SOL8-I | SOLC36-4-9 | C-side | No connector on LVPS side (cable inserted in LVPS sense connector); BURNDY on potence side 8I | 1 | 0 | 15 (tbc) | N | 0 | N | N | N | 1 cable = 9 pairs of sense = 9x2 0.5 mm2 NE18 == 1 half-chamber station 4; length is approximative; cable between LVPS and potence
90 | MCH | Sense SOLAR |  |  | 04.21.52.130.6 | 0.5 mm2 | SOL8-I | SOLC36-4-10 | C-side | No connector on LVPS side (cable inserted in LVPS sense connector); BURNDY on potence side 8I | 1 | 0 | 15 (tbc) | N | 0 | N | N | N | 1 cable = 9 pairs of sense = 9x2 0.5 mm2 NE18 == 1 half-chamber station 4; length is approximative; cable between LVPS and potence
91 | MCH | Sense SOLAR |  |  | 04.21.52.130.6 | 0.5 mm2 | SOL8-I | SOLC36-4-11 | C-side | No connector on LVPS side (cable inserted in LVPS sense connector); BURNDY on potence side 8I | 1 | 0 | 15 (tbc) | N | 0 | N | N | N | 1 cable = 9 pairs of sense = 9x2 0.5 mm2 NE18 == 1 half-chamber station 4; length is approximative; cable between LVPS and potence
92 | MCH | Sense SOLAR |  |  | 04.21.52.130.6 | 0.5 mm2 | SOL8-I | SOLC36-4-12 | C-side | No connector on LVPS side (cable inserted in LVPS sense connector); BURNDY on potence side 8I | 1 | 0 | 15 (tbc) | N | 0 | N | N | N | 1 cable = 9 pairs of sense = 9x2 0.5 mm2 NE18 == 1 half-chamber station 4; length is approximative; cable between LVPS and potence
93 | MCH | Sense SOLAR |  |  | 04.21.52.130.6 | 0.5 mm2 | SOL8-I | SOLC36-5-1 | C-side | No connector on LVPS side (cable inserted in LVPS sense connector); BURNDY on potence side 8I | 1 | 0 | 15 (tbc) | N | 0 | N | N | N | 1 cable = 9 pairs of sense = 9x2 0.5 mm2 NE18 == 1 half-chamber station 4; length is approximative; cable between LVPS and potence
94 | MCH | Sense SOLAR |  |  | 04.21.52.130.6 | 0.5 mm2 | SOL8-I | SOLC36-5-2 | C-side | No connector on LVPS side (cable inserted in LVPS sense connector); BURNDY on potence side 8I | 1 | 0 | 15 (tbc) | N | 0 | N | N | N | 1 cable = 9 pairs of sense = 9x2 0.5 mm2 NE18 == 1 half-chamber station 4; length is approximative; cable between LVPS and potence
95 | MCH | Sense SOLAR |  |  | 04.21.52.130.6 | 0.5 mm2 | SOL9-I | SOLC36-5-3 | C-side | No connector on LVPS side (cable inserted in LVPS sense connector); BURNDY on potence side 9I | 1 | 0 | 15 (tbc) | N | 0 | N | N | N | 1 cable = 9 pairs of sense = 9x2 0.5 mm2 NE18 == 1 half-chamber station 5; length is approximative; cable between LVPS and potence
96 | MCH | Sense SOLAR |  |  | 04.21.52.130.6 | 0.5 mm2 | SOL9-I | SOLC36-5-4 | C-side | No connector on LVPS side (cable inserted in LVPS sense connector); BURNDY on potence side 9I | 1 | 0 | 15 (tbc) | N | 0 | N | N | N | 1 cable = 9 pairs of sense = 9x2 0.5 mm2 NE18 == 1 half-chamber station 5; length is approximative; cable between LVPS and potence
97 | MCH | Sense SOLAR |  |  | 04.21.52.130.6 | 0.5 mm2 | SOL9-I | SOLC36-5-5 | C-side | No connector on LVPS side (cable inserted in LVPS sense connector); BURNDY on potence side 9I | 1 | 0 | 15 (tbc) | N | 0 | N | N | N | 1 cable = 9 pairs of sense = 9x2 0.5 mm2 NE18 == 1 half-chamber station 5; length is approximative; cable between LVPS and potence
98 | MCH | Sense SOLAR |  |  | 04.21.52.130.6 | 0.5 mm2 | SOL9-OI | SOLC36-5-6 | C-side | No connector on LVPS side (cable inserted in LVPS sense connector); BURNDY on potence side 9I | 1 | 0 | 15 (tbc) | N | 0 | N | N | N | 1 cable = 9 pairs of sense = 9x2 0.5 mm2 NE18 == 1 half-chamber station 5; length is approximative; cable between LVPS and potence
99 | MCH | Sense SOLAR |  |  | 04.21.52.130.6 | 0.5 mm2 | SOL9-I | SOLC36-5-7 | C-side | No connector on LVPS side (cable inserted in LVPS sense connector); BURNDY on potence side 9I | 1 | 0 | 15 (tbc) | N | 0 | N | N | N | 1 cable = 9 pairs of sense = 9x2 0.5 mm2 NE18 == 1 half-chamber station 5; length is approximative; cable between LVPS and potence
100 | MCH | Sense SOLAR |  |  | 04.21.52.130.6 | 0.5 mm2 | SOL9-I | SOLC36-5-8 | C-side | No connector on LVPS side (cable inserted in LVPS sense connector); BURNDY on potence side 9I | 1 | 0 | 15 (tbc) | N | 0 | N | N | N | 1 cable = 9 pairs of sense = 9x2 0.5 mm2 NE18 == 1 half-chamber station 5; length is approximative; cable between LVPS and potence
101 | MCH | Sense SOLAR |  |  | 04.21.52.130.6 | 0.5 mm2 | SOL9-I | SOLC36-5-9 | C-side | No connector on LVPS side (cable inserted in LVPS sense connector); BURNDY on potence side 9I | 1 | 0 | 15 (tbc) | N | 0 | N | N | N | 1 cable = 9 pairs of sense = 9x2 0.5 mm2 NE18 == 1 half-chamber station 5; length is approximative; cable between LVPS and potence
102 | MCH | Sense SOLAR |  |  | 04.21.52.130.6 | 0.5 mm2 | SOL9-I | SOLC36-5-10 | C-side | No connector on LVPS side (cable inserted in LVPS sense connector); BURNDY on potence side 9I | 1 | 0 | 15 (tbc) | N | 0 | N | N | N | 1 cable = 9 pairs of sense = 9x2 0.5 mm2 NE18 == 1 half-chamber station 5; length is approximative; cable between LVPS and potence
103 | MCH | Sense SOLAR |  |  | 04.21.52.130.6 | 0.5 mm2 | SOL10-I | SOLC36-6-1 | C-side | No connector on LVPS side (cable inserted in LVPS sense connector); BURNDY on potence side 10I | 1 | 0 | 15 (tbc) | N | 0 | N | N | N | 1 cable = 9 pairs of sense = 9x2 0.5 mm2 NE18 == 1 half-chamber station 5; length is approximative; cable between LVPS and potence
104 | MCH | Sense SOLAR |  |  | 04.21.52.130.6 | 0.5 mm2 | SOL10-I | SOLC36-6-2 | C-side | No connector on LVPS side (cable inserted in LVPS sense connector); BURNDY on potence side 10I | 1 | 0 | 15 (tbc) | N | 0 | N | N | N | 1 cable = 9 pairs of sense = 9x2 0.5 mm2 NE18 == 1 half-chamber station 5; length is approximative; cable between LVPS and potence
105 | MCH | Sense SOLAR |  |  | 04.21.52.130.6 | 0.5 mm2 | SOL10-I | SOLC36-6-3 | C-side | No connector on LVPS side (cable inserted in LVPS sense connector); BURNDY on potence side 10I | 1 | 0 | 15 (tbc) | N | 0 | N | N | N | 1 cable = 9 pairs of sense = 9x2 0.5 mm2 NE18 == 1 half-chamber station 5; length is approximative; cable between LVPS and potence
106 | MCH | Sense SOLAR |  |  | 04.21.52.130.6 | 0.5 mm2 | SOL10-I | SOLC36-6-4 | C-side | No connector on LVPS side (cable inserted in LVPS sense connector); BURNDY on potence side 10I | 1 | 0 | 15 (tbc) | N | 0 | N | N | N | 1 cable = 9 pairs of sense = 9x2 0.5 mm2 NE18 == 1 half-chamber station 5; length is approximative; cable between LVPS and potence
107 | MCH | Sense SOLAR |  |  | 04.21.52.130.6 | 0.5 mm2 | SOL10-I | SOLC36-6-5 | C-side | No connector on LVPS side (cable inserted in LVPS sense connector); BURNDY on potence side 10I | 1 | 0 | 15 (tbc) | N | 0 | N | N | N | 1 cable = 9 pairs of sense = 9x2 0.5 mm2 NE18 == 1 half-chamber station 5; length is approximative; cable between LVPS and potence
108 | MCH | Sense SOLAR |  |  | 04.21.52.130.6 | 0.5 mm2 | SOL10-I | SOLC36-6-6 | C-side | No connector on LVPS side (cable inserted in LVPS sense connector); BURNDY on potence side 10I | 1 | 0 | 15 (tbc) | N | 0 | N | N | N | 1 cable = 9 pairs of sense = 9x2 0.5 mm2 NE18 == 1 half-chamber station 5; length is approximative; cable between LVPS and potence
109 | MCH | Sense SOLAR |  |  | 04.21.52.130.6 | 0.5 mm2 | SOL10-I | SOLC36-6-7 | C-side | No connector on LVPS side (cable inserted in LVPS sense connector); BURNDY on potence side 10I | 1 | 0 | 15 (tbc) | N | 0 | N | N | N | 1 cable = 9 pairs of sense = 9x2 0.5 mm2 NE18 == 1 half-chamber station 5; length is approximative; cable between LVPS and potence
110 | MCH | Sense SOLAR |  |  | 04.21.52.130.6 | 0.5 mm2 | SOL10-I | SOLC36-6-8 | C-side | No connector on LVPS side (cable inserted in LVPS sense connector); BURNDY on potence side 10I | 1 | 0 | 15 (tbc) | N | 0 | N | N | N | 1 cable = 9 pairs of sense = 9x2 0.5 mm2 NE18 == 1 half-chamber station 5; length is approximative; cable between LVPS and potence
LV SOLAR on potence INSIDE
197 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL7-I | SOL7-I-C1 | C-side | On potence side STAUBLI 7I; no connector on SOLAR crate side (cable inserted in WAGO 826-164) | 1 | 0 | 4,5 (tbc) | N | 0 | N | N | N | cable on CH7I potence (Station 4): 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative ; cable between Bottom Potence and SOLAR crate
198 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL7-I | SOL7-I-C2 | C-side | On potence side STAUBLI 7I; no connector on SOLAR crate side | 1 | 0 | 4 (tbc) | N | 0 | N | N | N | cable on CH7I potence (Station 4): 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative ; cable between Bottom Potence and SOLAR crate
199 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL7-I | SOL7-I-C3 | C-side | On potence side STAUBLI 7I; no connector on SOLAR crate side | 1 | 0 | 3,5 (tbc) | N | 0 | N | N | N | cable on CH7I potence (Station 4): 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative ; cable between Bottom Potence and SOLAR crate
200 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL7-I | SOL7-I-C4 | C-side | On potence side STAUBLI 7I; no connector on SOLAR crate side | 1 | 0 | 3 (tbc) | N | 0 | N | N | N | cable on CH7I potence (Station 4): 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative ; cable between Bottom Potence and SOLAR crate
201 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL7-I | SOL7-I-C5 | C-side | On potence side STAUBLI 7I; no connector on SOLAR crate side | 1 | 0 | 2,5 (tbc) | N | 0 | N | N | N | cable on CH7I potence (Station 4): 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative ; cable between Bottom Potence and SOLAR crate
202 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL7-I | SOL7-I-C6 | C-side | On potence side STAUBLI 7I; no connector on SOLAR crate side | 1 | 0 | 2 (tbc) | N | 0 | N | N | N | cable on CH7I potence (Station 4): 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative ; cable between Bottom Potence and SOLAR crate
203 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL7-I | SOL7-I-C7 | C-side | On potence side STAUBLI 7I; no connector on SOLAR crate side | 1 | 0 | 1,5 (tbc) | N | 0 | N | N | N | cable on CH7I potence (Station 4): 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative ; cable between Bottom Potence and SOLAR crate
204 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL8-I | SOL8-I-C1 | C-side | On potence side STAUBLI 8I; no connector on SOLAR crate side | 1 | 0 | 4,5 (tbc) | N | 0 | N | N | N | cable on CH8I potence (Station 4): 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative ; cable between Bottom Potence and SOLAR crate
205 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL8-I | SOL8-I-C2 | C-side | On potence side STAUBLI 8I; no connector on SOLAR crate side | 1 | 0 | 4 (tbc) | N | 0 | N | N | N | cable on CH8I potence (Station 4): 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative ; cable between Bottom Potence and SOLAR crate
206 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL8-I | SOL8-I-C3 | C-side | On potence side STAUBLI 8I; no connector on SOLAR crate side | 1 | 0 | 3,5 (tbc) | N | 0 | N | N | N | cable on CH8I potence (Station 4): 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative ; cable between Bottom Potence and SOLAR crate
207 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL8-I | SOL8-I-C4 | C-side | On potence side STAUBLI 8I; no connector on SOLAR crate side | 1 | 0 | 3 (tbc) | N | 0 | N | N | N | cable on CH8I potence (Station 4): 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative ; cable between Bottom Potence and SOLAR crate
208 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL8-I | SOL8-I-C5 | C-side | On potence side STAUBLI 8I; no connector on SOLAR crate side | 1 | 0 | 2,5 (tbc) | N | 0 | N | N | N | cable on CH8I potence (Station 4): 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative ; cable between Bottom Potence and SOLAR crate
209 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL8-I | SOL8-I-C6 | C-side | On potence side STAUBLI 8I; no connector on SOLAR crate side | 1 | 0 | 2 (tbc) | N | 0 | N | N | N | cable on CH8I potence (Station 4): 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative ; cable between Bottom Potence and SOLAR crate
210 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL8-I | SOL8-I-C7 | C-side | On potence side STAUBLI 8I; no connector on SOLAR crate side | 1 | 0 | 1,5 (tbc) | N | 0 | N | N | N | cable on CH8I potence (Station 4): 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative ; cable between Bottom Potence and SOLAR crate
211 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL9-I | SOL9-I-C1 | C-side | On potence side STAUBLI 9I; no connector on SOLAR crate side | 1 | 0 | 5 (tbc) | N | 0 | N | N | N | cable on CH9I potence (Station 5): 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative ; cable between Bottom Potence and SOLAR crate
212 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL9-I | SOL9-I-C2 | C-side | On potence side STAUBLI 9I; no connector on SOLAR crate side | 1 | 0 | 4,5 (tbc) | N | 0 | N | N | N | cable on CH9I potence (Station 5): 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative ; cable between Bottom Potence and SOLAR crate
213 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL9-I | SOL9-I-C3 | C-side | On potence side STAUBLI 9I; no connector on SOLAR crate side | 1 | 0 | 4 (tbc) | N | 0 | N | N | N | cable on CH9I potence (Station 5): 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative ; cable between Bottom Potence and SOLAR crate
214 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL9-I | SOL9-I-C4 | C-side | On potence side STAUBLI 9I; no connector on SOLAR crate side | 1 | 0 | 3,5 (tbc) | N | 0 | N | N | N | cable on CH9I potence (Station 5): 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative ; cable between Bottom Potence and SOLAR crate
215 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL9-I | SOL9-I-C5 | C-side | On potence side STAUBLI 9I; no connector on SOLAR crate side | 1 | 0 | 3 (tbc) | N | 0 | N | N | N | cable on CH9I potence (Station 5): 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative ; cable between Bottom Potence and SOLAR crate
216 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL9-I | SOL9-I-C6 | C-side | On potence side STAUBLI 9I; no connector on SOLAR crate side | 1 | 0 | 2,5 (tbc) | N | 0 | N | N | N | cable on CH9I potence (Station 5): 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative ; cable between Bottom Potence and SOLAR crate
217 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL9-I | SOL9-I-C7 | C-side | On potence side STAUBLI 9I; no connector on SOLAR crate side | 1 | 0 | 2 (tbc) | N | 0 | N | N | N | cable on CH9I potence (Station 5): 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative ; cable between Bottom Potence and SOLAR crate
218 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL9-I | SOL9-I-C8 | C-side | On potence side STAUBLI 9I; no connector on SOLAR crate side | 1 | 0 | 1,5 (tbc) | N | 0 | N | N | N | cable on CH9I potence (Station 5): 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative ; cable between Bottom Potence and SOLAR crate
219 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL10-I | SOL10-I-C1 | C-side | On potence side STAUBLI 10I; no connector on SOLAR crate side | 1 | 0 | 5 (tbc) | N | 0 | N | N | N | cable on CH10I potence (Station 5): 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative ; cable between Bottom Potence and SOLAR crate
220 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL10-I | SOL10-I-C2 | C-side | On potence side STAUBLI 10I; no connector on SOLAR crate side | 1 | 0 | 4,5 (tbc) | N | 0 | N | N | N | cable on CH10I potence (Station 5): 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative ; cable between Bottom Potence and SOLAR crate
221 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL10-I | SOL10-I-C3 | C-side | On potence side STAUBLI 10I; no connector on SOLAR crate side | 1 | 0 | 4 (tbc) | N | 0 | N | N | N | cable on CH10I potence (Station 5): 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative ; cable between Bottom Potence and SOLAR crate
222 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL10-I | SOL10-I-C4 | C-side | On potence side STAUBLI 10I; no connector on SOLAR crate side | 1 | 0 | 3,5 (tbc) | N | 0 | N | N | N | cable on CH10I potence (Station 5): 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative ; cable between Bottom Potence and SOLAR crate
223 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL10-I | SOL10-I-C5 | C-side | On potence side STAUBLI 10I; no connector on SOLAR crate side | 1 | 0 | 3 (tbc) | N | 0 | N | N | N | cable on CH10I potence (Station 5): 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative ; cable between Bottom Potence and SOLAR crate
224 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL10-I | SOL10-I-C6 | C-side | On potence side STAUBLI 10I; no connector on SOLAR crate side | 1 | 0 | 2,5 (tbc) | N | 0 | N | N | N | cable on CH10I potence (Station 5): 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative ; cable between Bottom Potence and SOLAR crate
225 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL10-I | SOL10-I-C7 | C-side | On potence side STAUBLI 10I; no connector on SOLAR crate side | 1 | 0 | 2 (tbc) | N | 0 | N | N | N | cable on CH10I potence (Station 5): 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative ; cable between Bottom Potence and SOLAR crate
226 | MCH | LV (SOLAR crates) | 5 | 10 | 04.08.61.454.0 | AWG11 | SOL10-I | SOL10-I-C8 | C-side | On potence side STAUBLI 10I; no connector on SOLAR crate side | 1 | 0 | 1,5 (tbc) | N | 0 | N | N | N | cable on CH10I potence (Station 5): 1 cable = 1 LV 4 mm2 + 1 ground 4 mm2; length is approximative ; cable between Bottom Potence and SOLAR crate
Sense SOLAR on potence INSIDE
197 | MCH | Sense (SOLAR crate) |  |  | 04.21.52.130.6 | 0.5 mm2 | SOL7-I | SOL7-I-C1 | C-side | On potence side BURNDY7I; no connector on SOLAR crate side (cable inserted in WAGO 826-164) | 1 | 0 | 4,5 (tbc) | N | 0 | N | N | N | cable on CH7I potence (Station 4):1 cable = 9 pairs of sense = 9x2 0.5 mm2 NE18 == 1 half-chamber station 4; length is approximative; cable between potence and SOLAR crate
198 | MCH | Sense SOLAR |  |  | 04.21.52.130.6 | 0.5 mm2 | SOL7-I | SOL7-I-C2 | C-side | On potence side BURNDY7I; no connector on SOLAR crate side | 1 | 0 | 4 (tbc) | N | 0 | N | N | N | cable on CH7I potence (Station 4):1 cable = 9 pairs of sense = 9x2 0.5 mm2 NE18 == 1 half-chamber station 4; length is approximative; cable between potence and SOLAR crate
199 | MCH | Sense SOLAR |  |  | 04.21.52.130.6 | 0.5 mm2 | SOL7-I | SOL7-I-C3 | C-side | On potence side BURNDY7I; no connector on SOLAR crate side | 1 | 0 | 3,5 (tbc) | N | 0 | N | N | N | cable on CH7I potence (Station 4):1 cable = 9 pairs of sense = 9x2 0.5 mm2 NE18 == 1 half-chamber station 4; length is approximative; cable between potence and SOLAR crate
200 | MCH | Sense SOLAR |  |  | 04.21.52.130.6 | 0.5 mm2 | SOL7-I | SOL7-I-C4 | C-side | On potence side BURNDY7I; no connector on SOLAR crate side | 1 | 0 | 3 (tbc) | N | 0 | N | N | N | cable on CH7I potence (Station 4):1 cable = 9 pairs of sense = 9x2 0.5 mm2 NE18 == 1 half-chamber station 4; length is approximative; cable between potence and SOLAR crate
201 | MCH | Sense SOLAR |  |  | 04.21.52.130.6 | 0.5 mm2 | SOL7-I | SOL7-I-C5 | C-side | On potence side BURNDY7I; no connector on SOLAR crate side | 1 | 0 | 2,5 (tbc) | N | 0 | N | N | N | cable on CH7I potence (Station 4):1 cable = 9 pairs of sense = 9x2 0.5 mm2 NE18 == 1 half-chamber station 4; length is approximative; cable between potence and SOLAR crate
202 | MCH | Sense SOLAR |  |  | 04.21.52.130.6 | 0.5 mm2 | SOL7-I | SOL7-I-C6 | C-side | On potence side BURNDY7I; no connector on SOLAR crate side | 1 | 0 | 2 (tbc) | N | 0 | N | N | N | cable on CH7I potence (Station 4):1 cable = 9 pairs of sense = 9x2 0.5 mm2 NE18 == 1 half-chamber station 4; length is approximative; cable between potence and SOLAR crate
203 | MCH | Sense SOLAR |  |  | 04.21.52.130.6 | 0.5 mm2 | SOL7-I | SOL7-I-C7 | C-side | On potence side BURNDY7I; no connector on SOLAR crate side | 1 | 0 | 1,5 (tbc) | N | 0 | N | N | N | cable on CH7I potence (Station 4):1 cable = 9 pairs of sense = 9x2 0.5 mm2 NE18 == 1 half-chamber station 4; length is approximative; cable between potence and SOLAR crate
204 | MCH | Sense SOLAR |  |  | 04.21.52.130.6 | 0.5 mm2 | SOL8-I | SOL8-I-C1 | C-side | On potence side BURNDY 8I; no connector on SOLAR crate side | 1 | 0 | 4,5 (tbc) | N | 0 | N | N | N | cable on CH8I potence (Station 4):1 cable = 9 pairs of sense = 9x2 0.5 mm2 NE18 == 1 half-chamber station 4; length is approximative; cable between potence and SOLAR crate
205 | MCH | Sense SOLAR |  |  | 04.21.52.130.6 | 0.5 mm2 | SOL8-I | SOL8-I-C2 | C-side | On potence side BURNDY 8I; no connector on SOLAR crate side | 1 | 0 | 4 (tbc) | N | 0 | N | N | N | cable on CH8I potence (Station 4):1 cable = 9 pairs of sense = 9x2 0.5 mm2 NE18 == 1 half-chamber station 4; length is approximative; cable between potence and SOLAR crate
206 | MCH | Sense SOLAR |  |  | 04.21.52.130.6 | 0.5 mm2 | SOL8-I | SOL8-I-C3 | C-side | On potence side BURNDY 8I; no connector on SOLAR crate side | 1 | 0 | 3,5 (tbc) | N | 0 | N | N | N | cable on CH8I potence (Station 4):1 cable = 9 pairs of sense = 9x2 0.5 mm2 NE18 == 1 half-chamber station 4; length is approximative; cable between potence and SOLAR crate
207 | MCH | Sense SOLAR |  |  | 04.21.52.130.6 | 0.5 mm2 | SOL8-I | SOL8-I-C4 | C-side | On potence side BURNDY 8I; no connector on SOLAR crate side | 1 | 0 | 3 (tbc) | N | 0 | N | N | N | cable on CH8I potence (Station 4):1 cable = 9 pairs of sense = 9x2 0.5 mm2 NE18 == 1 half-chamber station 4; length is approximative; cable between potence and SOLAR crate
208 | MCH | Sense SOLAR |  |  | 04.21.52.130.6 | 0.5 mm2 | SOL8-I | SOL8-I-C5 | C-side | On potence side BURNDY 8I; no connector on SOLAR crate side | 1 | 0 | 2,5 (tbc) | N | 0 | N | N | N | cable on CH8I potence (Station 4):1 cable = 9 pairs of sense = 9x2 0.5 mm2 NE18 == 1 half-chamber station 4; length is approximative; cable between potence and SOLAR crate
209 | MCH | Sense SOLAR |  |  | 04.21.52.130.6 | 0.5 mm2 | SOL8-I | SOL8-I-C6 | C-side | On potence side BURNDY 8I; no connector on SOLAR crate side | 1 | 0 | 2 (tbc) | N | 0 | N | N | N | cable on CH8I potence (Station 4):1 cable = 9 pairs of sense = 9x2 0.5 mm2 NE18 == 1 half-chamber station 4; length is approximative; cable between potence and SOLAR crate
210 | MCH | Sense SOLAR |  |  | 04.21.52.130.6 | 0.5 mm2 | SOL8-I | SOL8-I-C7 | C-side | On potence side BURNDY 8I; no connector on SOLAR crate side | 1 | 0 | 1,5 (tbc) | N | 0 | N | N | N | cable on CH8I potence (Station 4):1 cable = 9 pairs of sense = 9x2 0.5 mm2 NE18 == 1 half-chamber station 4; length is approximative; cable between potence and SOLAR crate
211 | MCH | Sense SOLAR |  |  | 04.21.52.130.6 | 0.5 mm2 | SOL9-I | SOL9-I-C1 | C-side | On potence side BURNDY 9I; no connector on SOLAR crate side | 1 | 0 | 5 (tbc) | N | 0 | N | N | N | cable on CH9I potence (Station 5):1 cable = 9 pairs of sense = 9x2 0.5 mm2 NE18 == 1 half-chamber station 4; length is approximative; cable between potence and SOLAR crate
212 | MCH | Sense SOLAR |  |  | 04.21.52.130.6 | 0.5 mm2 | SOL9-I | SOL9-I-C2 | C-side | On potence side BURNDY 9I; no connector on SOLAR crate side | 1 | 0 | 4,5 (tbc) | N | 0 | N | N | N | cable on CH9I potence (Station 5):1 cable = 9 pairs of sense = 9x2 0.5 mm2 NE18 == 1 half-chamber station 4; length is approximative; cable between potence and SOLAR crate
213 | MCH | Sense SOLAR |  |  | 04.21.52.130.6 | 0.5 mm2 | SOL9-I | SOL9-I-C3 | C-side | On potence side BURNDY 9O; no connector on SOLAR crate side | 1 | 0 | 4 (tbc) | N | 0 | N | N | N | cable on CH9I potence (Station 5):1 cable = 9 pairs of sense = 9x2 0.5 mm2 NE18 == 1 half-chamber station 4; length is approximative; cable between potence and SOLAR crate
214 | MCH | Sense SOLAR |  |  | 04.21.52.130.6 | 0.5 mm2 | SOL9-I | SOL9-I-C4 | C-side | On potence side BURNDY 9O; no connector on SOLAR crate side | 1 | 0 | 3,5 (tbc) | N | 0 | N | N | N | cable on CH9I potence (Station 5):1 cable = 9 pairs of sense = 9x2 0.5 mm2 NE18 == 1 half-chamber station 4; length is approximative; cable between potence and SOLAR crate
215 | MCH | Sense SOLAR |  |  | 04.21.52.130.6 | 0.5 mm2 | SOL9-I | SOL9-I-C5 | C-side | On potence side BURNDY 9O; no connector on SOLAR crate side | 1 | 0 | 3 (tbc) | N | 0 | N | N | N | cable on CH9I potence (Station 5):1 cable = 9 pairs of sense = 9x2 0.5 mm2 NE18 == 1 half-chamber station 4; length is approximative; cable between potence and SOLAR crate
216 | MCH | Sense SOLAR |  |  | 04.21.52.130.6 | 0.5 mm2 | SOL9-I | SOL9-I-C6 | C-side | On potence side BURNDY 9O; no connector on SOLAR crate side | 1 | 0 | 2,5 (tbc) | N | 0 | N | N | N | cable on CH9I potence (Station 5):1 cable = 9 pairs of sense = 9x2 0.5 mm2 NE18 == 1 half-chamber station 4; length is approximative; cable between potence and SOLAR crate
217 | MCH | Sense SOLAR |  |  | 04.21.52.130.6 | 0.5 mm2 | SOL9-I | SOL9-I-C7 | C-side | On potence side BURNDY 9O; no connector on SOLAR crate side | 1 | 0 | 2 (tbc) | N | 0 | N | N | N | cable on CH9I potence (Station 5):1 cable = 9 pairs of sense = 9x2 0.5 mm2 NE18 == 1 half-chamber station 4; length is approximative; cable between potence and SOLAR crate
218 | MCH | Sense SOLAR |  |  | 04.21.52.130.6 | 0.5 mm2 | SOL9-I | SOL9-I-C8 | C-side | On potence side BURNDY 9I; no connector on SOLAR crate side | 1 | 0 | 1,5 (tbc) | N | 0 | N | N | N | cable on CH9I potence (Station 5):1 cable = 9 pairs of sense = 9x2 0.5 mm2 NE18 == 1 half-chamber station 4; length is approximative; cable between potence and SOLAR crate
219 | MCH | Sense SOLAR |  |  | 04.21.52.130.6 | 0.5 mm2 | SOL10-I | SOL10-I-C1 | C-side | On potence side BURNDY 10I; no connector on SOLAR crate side | 1 | 0 | 5 (tbc) | N | 0 | N | N | N | cable on CH10I potence (Station 5):1 cable = 9 pairs of sense = 9x2 0.5 mm2 NE18 == 1 half-chamber station 4; length is approximative; cable between potence and SOLAR crate
220 | MCH | Sense SOLAR |  |  | 04.21.52.130.6 | 0.5 mm2 | SOL10-I | SOL10-I-C2 | C-side | On potence side BURNDY 10I; no connector on SOLAR crate side | 1 | 0 | 4,5 (tbc) | N | 0 | N | N | N | cable on CH10I potence (Station 5):1 cable = 9 pairs of sense = 9x2 0.5 mm2 NE18 == 1 half-chamber station 4; length is approximative; cable between potence and SOLAR crate
221 | MCH | Sense SOLAR |  |  | 04.21.52.130.6 | 0.5 mm2 | SOL10-I | SOL10-I-C3 | C-side | On potence side BURNDY 10I; no connector on SOLAR crate side | 1 | 0 | 4 (tbc) | N | 0 | N | N | N | cable on CH10I potence (Station 5):1 cable = 9 pairs of sense = 9x2 0.5 mm2 NE18 == 1 half-chamber station 4; length is approximative; cable between potence and SOLAR crate
222 | MCH | Sense SOLAR |  |  | 04.21.52.130.6 | 0.5 mm2 | SOL10-I | SOL10-I-C4 | C-side | On potence side BURNDY 10I; no connector on SOLAR crate side | 1 | 0 | 3,5 (tbc) | N | 0 | N | N | N | cable on CH10I potence (Station 5):1 cable = 9 pairs of sense = 9x2 0.5 mm2 NE18 == 1 half-chamber station 4; length is approximative; cable between potence and SOLAR crate
223 | MCH | Sense SOLAR |  |  | 04.21.52.130.6 | 0.5 mm2 | SOL10-I | SOL10-I-C5 | C-side | On potence side BURNDY 10I; no connector on SOLAR crate side | 1 | 0 | 3 (tbc) | N | 0 | N | N | N | cable on CH10I potence (Station 5):1 cable = 9 pairs of sense = 9x2 0.5 mm2 NE18 == 1 half-chamber station 4; length is approximative; cable between potence and SOLAR crate
224 | MCH | Sense SOLAR |  |  | 04.21.52.130.6 | 0.5 mm2 | SOL10-I | SOL10-I-C6 | C-side | On potence side BURNDY 10I; no connector on SOLAR crate side | 1 | 0 | 2,5 (tbc) | N | 0 | N | N | N | cable on CH10I potence (Station 5):1 cable = 9 pairs of sense = 9x2 0.5 mm2 NE18 == 1 half-chamber station 4; length is approximative; cable between potence and SOLAR crate
225 | MCH | Sense SOLAR |  |  | 04.21.52.130.6 | 0.5 mm2 | SOL10-I | SOL10-I-C7 | C-side | On potence side BURNDY 10I; no connector on SOLAR crate side | 1 | 0 | 2 (tbc) | N | 0 | N | N | N | cable on CH10I potence (Station 5):1 cable = 9 pairs of sense = 9x2 0.5 mm2 NE18 == 1 half-chamber station 4; length is approximative; cable between potence and SOLAR crate
226 | MCH | Sense SOLAR |  |  | 04.21.52.130.6 | 0.5 mm2 | SOL10-I | SOL10-I-C8 | C-side | On potence side BURNDY 10I; no connector on SOLAR crate side | 1 | 0 | 1,5 (tbc) | N | 0 | N | N | N | cable on CH10I potence (Station 5):1 cable = 9 pairs of sense = 9x2 0.5 mm2 NE18 == 1 half-chamber station 4; length is approximative; cable between potence and SOLAR crate
MCH LV FEC
LV FEC additional cables OUTSIDE
55 | MCH | LV FEC | 8 | 100 | 04.08.61.591.2 | AWG5 (16 mm2) | SOL1-O-C1 | SOLC09-1-1 | C-side | Bended lug M6 on LVPS side; straight lug M8 ?? in LV filter box | 1 | 0 | 25 (tbc) | N | 0 | N | N | N | 1 cable = 2 LV 16 mm2 + 2 ground 16 mm2; length is approximative; additional cable between LVPS and SOLAR crate
56 | MCH | LV FEC | 8 | 100 | 04.08.61.591.2 | AWG5 (16 mm2) | SOL1-O-C2 | SOLC09-1-2 | C-side | Bended lug M6 on LVPS side; straight lug M8 ?? in LV filter box | 1 | 0 | 25 (tbc) | N | 0 | N | N | N | 1 cable = 2 LV 16 mm2 + 2 ground 16 mm2; length is approximative; additional cable between LVPS and SOLAR crate
57 | MCH | LV FEC | 8 | 100 | 04.08.61.591.2 | AWG5 (16 mm2) | SOL1-O-C3 | SOLC09-1-3 | C-side | Bended lug M6 on LVPS side; straight lug M8 ?? in LV filter box | 1 | 0 | 25 (tbc) | N | 0 | N | N | N | 1 cable = 2 LV 16 mm2 + 2 ground 16 mm2; length is approximative; additional cable between LVPS and SOLAR crate
58 | MCH | LV FEC | 8 | 100 | 04.08.61.591.2 | AWG5 (16 mm2) | SOL1-O-C4 | SOLC09-2-1 | C-side | Bended lug M6 on LVPS side; straight lug M8 ?? in LV filter box | 1 | 0 | 25 (tbc) | N | 0 | N | N | N | 1 cable = 2 LV 16 mm2 + 2 ground 16 mm2; length is approximative; additional cable between LVPS and SOLAR crate
59 | MCH | LV FEC | 8 | 100 | 04.08.61.591.2 | AWG5 (16 mm2) | SOL2-O-C1 | SOLC09-2-2 | C-side | Bended lug M6 on LVPS side; straight lug M8 ?? in LV filter box | 1 | 0 | 25 (tbc) | N | 0 | N | N | N | 1 cable = 2 LV 16 mm2 + 2 ground 16 mm2; length is approximative; additional cable between LVPS and SOLAR crate
60 | MCH | LV FEC | 8 | 100 | 04.08.61.591.2 | AWG5 (16 mm2) | SOL2-O-C2 | SOLC09-2-3 | C-side | Bended lug M6 on LVPS side; straight lug M8 ?? in LV filter box | 1 | 0 | 25 (tbc) | N | 0 | N | N | N | 1 cable = 2 LV 16 mm2 + 2 ground 16 mm2; length is approximative; additional cable between LVPS and SOLAR crate
61 | MCH | LV FEC | 8 | 100 | 04.08.61.591.2 | AWG5 (16 mm2) | SOL2-O-C3 | SOLC09-3-1 | C-side | Bended lug M6 on LVPS side; straight lug M8 ?? in LV filter box | 1 | 0 | 25 (tbc) | N | 0 | N | N | N | 1 cable = 2 LV 16 mm2 + 2 ground 16 mm2; length is approximative; additional cable between LVPS and SOLAR crate
62 | MCH | LV FEC | 8 | 100 | 04.08.61.591.2 | AWG5 (16 mm2) | SOL2-O-C4 | SOLC09-3-2 | C-side | Bended lug M6 on LVPS side; straight lug M8 ?? in LV filter box | 1 | 0 | 25 (tbc) | N | 0 | N | N | N | 1 cable = 2 LV 16 mm2 + 2 ground 16 mm2; length is approximative; additional cable between LVPS and SOLAR crate
63 | MCH | LV FEC | 8 | 100 | 04.08.61.591.2 | AWG5 (16 mm2) | SOL3-O-C1 | SOLC09-3-3 | C-side | Bended lug M6 on LVPS side; straight lug M8 ?? in LV filter box | 1 | 0 | 25 (tbc) | N | 0 | N | N | N | 1 cable = 2 LV 16 mm2 + 2 ground 16 mm2; length is approximative; additional cable between LVPS and SOLAR crate
64 | MCH | LV FEC | 8 | 100 | 04.08.61.591.2 | AWG5 (16 mm2) | SOL3-O-C2 | SOLC09-4-1 | C-side | Bended lug M6 on LVPS side; straight lug M8 ?? in LV filter box | 1 | 0 | 25 (tbc) | N | 0 | N | N | N | 1 cable = 2 LV 16 mm2 + 2 ground 16 mm2; length is approximative; additional cable between LVPS and SOLAR crate
65 | MCH | LV FEC | 8 | 100 | 04.08.61.591.2 | AWG5 (16 mm2) | SOL3-O-C3 | SOLC09-4-2 | C-side | Bended lug M6 on LVPS side; straight lug M8 ?? in LV filter box | 1 | 0 | 25 (tbc) | N | 0 | N | N | N | 1 cable = 2 LV 16 mm2 + 2 ground 16 mm2; length is approximative; additional cable between LVPS and SOLAR crate
66 | MCH | LV FEC | 8 | 100 | 04.08.61.591.2 | AWG5 (16 mm2) | SOL3-O-C4 | SOLC09-4-3 | C-side | Bended lug M6 on LVPS side; straight lug M8 ?? in LV filter box | 1 | 0 | 25 (tbc) | N | 0 | N | N | N | 1 cable = 2 LV 16 mm2 + 2 ground 16 mm2; length is approximative; additional cable between LVPS and SOLAR crate
67 | MCH | LV FEC | 8 | 100 | 04.08.61.591.2 | AWG5 (16 mm2) | SOL4-O-C1 | SOLC09-5-1 | C-side | Bended lug M6 on LVPS side; straight lug M8 ?? in LV filter box | 1 | 0 | 25 (tbc) | N | 0 | N | N | N | 1 cable = 2 LV 16 mm2 + 2 ground 16 mm2; length is approximative; additional cable between LVPS and SOLAR crate
68 | MCH | LV FEC | 8 | 100 | 04.08.61.591.2 | AWG5 (16 mm2) | SOL4-O-C2 | SOLC09-5-2 | C-side | Bended lug M6 on LVPS side; straight lug M8 ?? in LV filter box | 1 | 0 | 25 (tbc) | N | 0 | N | N | N | 1 cable = 2 LV 16 mm2 + 2 ground 16 mm2; length is approximative; additional cable between LVPS and SOLAR crate
69 | MCH | LV FEC | 8 | 100 | 04.08.61.591.2 | AWG5 (16 mm2) | SOL4-O-C3 | SOLC09-5-3 | C-side | Bended lug M6 on LVPS side; straight lug M8 ?? in LV filter box | 1 | 0 | 25 (tbc) | N | 0 | N | N | N | 1 cable = 2 LV 16 mm2 + 2 ground 16 mm2; length is approximative; additional cable between LVPS and SOLAR crate
70 | MCH | LV FEC | 8 | 100 | 04.08.61.591.2 | AWG5 (16 mm2) | SOL4-O-C4 | SOLC10-1-1 | C-side | Bended lug M6 on LVPS side; straight lug M8 ?? in LV filter box | 1 | 0 | 25 (tbc) | N | 0 | N | N | N | 1 cable = 2 LV 16 mm2 + 2 ground 16 mm2; length is approximative; additional cable between LVPS and SOLAR crate
71 | MCH | LV FEC | 8 | 100 | 04.08.61.591.2 | AWG5 (16 mm2) | SOL5-O-C1 | SOLC10-2-1 | C-side | Bended lug M6 on LVPS side; straight lug M8 ?? in LV filter box | 1 | 0 | 20 (tbc) | N | 0 | N | N | N | 1 cable = 2 LV 16 mm2 + 2 ground 16 mm2; length is approximative; additional cable between LVPS and SOLAR crate
75 | MCH | LV FEC | 8 | 100 | 04.08.61.591.2 | AWG5 (16 mm2) | SOL5-O-C5 | SOLC10-3-1 | C-side | Bended lug M6 on LVPS side; straight lug M8 ?? in LV filter box | 1 | 0 | 20 (tbc) | N | 0 | N | N | N | 1 cable = 2 LV 16 mm2 + 2 ground 16 mm2; length is approximative; additional cable between LVPS and SOLAR crate
76 | MCH | LV FEC | 8 | 100 | 04.08.61.591.2 | AWG5 (16 mm2) | SOL6-O-C1 | SOLC10-3-2 | C-side | Bended lug M6 on LVPS side; straight lug M8 ?? in LV filter box | 1 | 0 | 20 (tbc) | N | 0 | N | N | N | 1 cable = 2 LV 16 mm2 + 2 ground 16 mm2; length is approximative; additional cable between LVPS and SOLAR crate
80 | MCH | LV FEC | 8 | 100 | 04.08.61.591.2 | AWG5 (16 mm2) | SOL6-O-C5 | SOLC10-3-4 | C-side | Bended lug M6 on LVPS side; straight lug M8 ?? in LV filter box |  | 0 | 20 (tbc) | N | 0 | N | N | N | 1 cable = 2 LV 16 mm2 + 2 ground 16 mm2; length is approximative; additional cable between LVPS and SOLAR crate
81 | MCH | LV FEC | 8 | 100 | 04.08.61.591.2 | AWG5 (16 mm2) | SOL7-O | SOLC10-5-1 | C-side | Bended lug M6 on LVPS side; connector BURNDY 4 pins (for 16 mm2 cable) | 1 | 0 | 15 (tbc) | N | 0 | N | N | N | 1 cable = 2 LV 16 mm2 + 2 ground 16 mm2; length is approximative; additional cable between LVPS and SOLAR crate
87 | MCH | LV FEC | 8 | 100 | 04.08.61.591.2 | AWG5 (16 mm2) | SOL7-O | SOLC11-1-2 | C-side | Bended lug M6 on LVPS side; connector BURNDY 4 pins (for 16 mm2 cable) | 1 | 0 | 15 (tbc) | N | 0 | N | N | N | 1 cable = 2 LV 16 mm2 + 2 ground 16 mm2; length is approximative; additional cable between LVPS and SOLAR crate
88 | MCH | LV FEC | 8 | 100 | 04.08.61.591.2 | AWG5 (16 mm2) | SOL8-O | SOLC11-1-3 | C-side | Bended lug M6 on LVPS side; connector BURNDY 4 pins (for 16 mm2 cable) | 1 | 0 | 15 (tbc) | N | 0 | N | N | N | 1 cable = 2 LV 16 mm2 + 2 ground 16 mm2; length is approximative; additional cable between LVPS and SOLAR crate
94 | MCH | LV FEC | 8 | 100 | 04.08.61.591.2 | AWG5 (16 mm2) | SOL8-O | SOLC11-2-5 | C-side | Bended lug M6 on LVPS side; connector BURNDY 4 pins (for 16 mm2 cable) | 1 | 0 | 15 (tbc) | N | 0 | N | N | N | 1 cable = 2 LV 16 mm2 + 2 ground 16 mm2; length is approximative; additional cable between LVPS and SOLAR crate
95 | MCH | LV FEC | 8 | 100 | 04.08.61.591.2 | AWG5 (16 mm2) | SOL9-O | SOLC11-3-1 | C-side | Bended lug M6 on LVPS side; connector BURNDY 4 pins (for 16 mm2 cable) | 1 | 0 | 15 (tbc) | N | 0 | N | N | N | 1 cable = 2 LV 16 mm2 + 2 ground 16 mm2; length is approximative; additional cable between LVPS and SOLAR crate
102 | MCH | LV FEC | 8 | 100 | 04.08.61.591.2 | AWG5 (16 mm2) | SOL9-O | SOLC11-4-2 | C-side | Bended lug M6 on LVPS side; connector BURNDY 4 pins (for 16 mm2 cable) | 1 | 0 | 15 (tbc) | N | 0 | N | N | N | 1 cable = 2 LV 16 mm2 + 2 ground 16 mm2; length is approximative; additional cable between LVPS and SOLAR crate
103 | MCH | LV FEC | 8 | 100 | 04.08.61.591.2 | AWG5 (16 mm2) | SOL10-O | SOLC11-4-3 | C-side | Bended lug M6 on LVPS side; connector BURNDY 4 pins (for 16 mm2 cable) | 1 | 0 | 15 (tbc) | N | 0 | N | N | N | 1 cable = 2 LV 16 mm2 + 2 ground 16 mm2; length is approximative; additional cable between LVPS and SOLAR crate
110 | MCH | LV FEC | 8 | 100 | 04.08.61.591.2 | AWG5 (16 mm2) | SOL10-O | SOLC11-5-5 | C-side | Bended lug M6 on LVPS side; connector BURNDY 4 pins (for 16 mm2 cable) | 1 | 0 | 15 (tbc) | N | 0 | N | N | N | 1 cable = 2 LV 16 mm2 + 2 ground 16 mm2; length is approximative; additional cable between LVPS and SOLAR crate
MCH sense FEC OUTSIDE???
LV FEC additional cables INSIDE
55 | MCH | LV FEC | 8 | 100 | 04.08.61.591.2 | AWG5 (16 mm2) | SOL1-O-C1 | SOLC37-1-1 | C-side | Bended lug M6 on LVPS side; straight lug M8 ?? in LV filter box | 1 | 0 | 25 (tbc) | N | 0 | N | N | N | 1 cable = 2 LV 16 mm2 + 2 ground 16 mm2; length is approximative; additional cable between LVPS and SOLAR crate
56 | MCH | LV FEC | 8 | 100 | 04.08.61.591.2 | AWG5 (16 mm2) | SOL1-O-C2 | SOLC37-1-2 | C-side | Bended lug M6 on LVPS side; straight lug M8 ?? in LV filter box | 1 | 0 | 25 (tbc) | N | 0 | N | N | N | 1 cable = 2 LV 16 mm2 + 2 ground 16 mm2; length is approximative; additional cable between LVPS and SOLAR crate
57 | MCH | LV FEC | 8 | 100 | 04.08.61.591.2 | AWG5 (16 mm2) | SOL1-O-C3 | SOLC37-1-3 | C-side | Bended lug M6 on LVPS side; straight lug M8 ?? in LV filter box | 1 | 0 | 25 (tbc) | N | 0 | N | N | N | 1 cable = 2 LV 16 mm2 + 2 ground 16 mm2; length is approximative; additional cable between LVPS and SOLAR crate
58 | MCH | LV FEC | 8 | 100 | 04.08.61.591.2 | AWG5 (16 mm2) | SOL1-O-C4 | SOLC37-2-1 | C-side | Bended lug M6 on LVPS side; straight lug M8 ?? in LV filter box | 1 | 0 | 25 (tbc) | N | 0 | N | N | N | 1 cable = 2 LV 16 mm2 + 2 ground 16 mm2; length is approximative; additional cable between LVPS and SOLAR crate
59 | MCH | LV FEC | 8 | 100 | 04.08.61.591.2 | AWG5 (16 mm2) | SOL2-O-C1 | SOLC37-2-2 | C-side | Bended lug M6 on LVPS side; straight lug M8 ?? in LV filter box | 1 | 0 | 25 (tbc) | N | 0 | N | N | N | 1 cable = 2 LV 16 mm2 + 2 ground 16 mm2; length is approximative; additional cable between LVPS and SOLAR crate
60 | MCH | LV FEC | 8 | 100 | 04.08.61.591.2 | AWG5 (16 mm2) | SOL2-O-C2 | SOLC37-2-3 | C-side | Bended lug M6 on LVPS side; straight lug M8 ?? in LV filter box | 1 | 0 | 25 (tbc) | N | 0 | N | N | N | 1 cable = 2 LV 16 mm2 + 2 ground 16 mm2; length is approximative; additional cable between LVPS and SOLAR crate
61 | MCH | LV FEC | 8 | 100 | 04.08.61.591.2 | AWG5 (16 mm2) | SOL2-O-C3 | SOLC37-3-1 | C-side | Bended lug M6 on LVPS side; straight lug M8 ?? in LV filter box | 1 | 0 | 25 (tbc) | N | 0 | N | N | N | 1 cable = 2 LV 16 mm2 + 2 ground 16 mm2; length is approximative; additional cable between LVPS and SOLAR crate
62 | MCH | LV FEC | 8 | 100 | 04.08.61.591.2 | AWG5 (16 mm2) | SOL2-O-C4 | SOLC37-3-2 | C-side | Bended lug M6 on LVPS side; straight lug M8 ?? in LV filter box | 1 | 0 | 25 (tbc) | N | 0 | N | N | N | 1 cable = 2 LV 16 mm2 + 2 ground 16 mm2; length is approximative; additional cable between LVPS and SOLAR crate
63 | MCH | LV FEC | 8 | 100 | 04.08.61.591.2 | AWG5 (16 mm2) | SOL3-O-C1 | SOLC37-3-3 | C-side | Bended lug M6 on LVPS side; straight lug M8 ?? in LV filter box | 1 | 0 | 25 (tbc) | N | 0 | N | N | N | 1 cable = 2 LV 16 mm2 + 2 ground 16 mm2; length is approximative; additional cable between LVPS and SOLAR crate
64 | MCH | LV FEC | 8 | 100 | 04.08.61.591.2 | AWG5 (16 mm2) | SOL3-O-C2 | SOLC37-4-1 | C-side | Bended lug M6 on LVPS side; straight lug M8 ?? in LV filter box | 1 | 0 | 25 (tbc) | N | 0 | N | N | N | 1 cable = 2 LV 16 mm2 + 2 ground 16 mm2; length is approximative; additional cable between LVPS and SOLAR crate
65 | MCH | LV FEC | 8 | 100 | 04.08.61.591.2 | AWG5 (16 mm2) | SOL3-O-C3 | SOLC37-4-2 | C-side | Bended lug M6 on LVPS side; straight lug M8 ?? in LV filter box | 1 | 0 | 25 (tbc) | N | 0 | N | N | N | 1 cable = 2 LV 16 mm2 + 2 ground 16 mm2; length is approximative; additional cable between LVPS and SOLAR crate
66 | MCH | LV FEC | 8 | 100 | 04.08.61.591.2 | AWG5 (16 mm2) | SOL3-O-C4 | SOLC37-4-3 | C-side | Bended lug M6 on LVPS side; straight lug M8 ?? in LV filter box | 1 | 0 | 25 (tbc) | N | 0 | N | N | N | 1 cable = 2 LV 16 mm2 + 2 ground 16 mm2; length is approximative; additional cable between LVPS and SOLAR crate
67 | MCH | LV FEC | 8 | 100 | 04.08.61.591.2 | AWG5 (16 mm2) | SOL4-O-C1 | SOLC37-5-1 | C-side | Bended lug M6 on LVPS side; straight lug M8 ?? in LV filter box | 1 | 0 | 25 (tbc) | N | 0 | N | N | N | 1 cable = 2 LV 16 mm2 + 2 ground 16 mm2; length is approximative; additional cable between LVPS and SOLAR crate
68 | MCH | LV FEC | 8 | 100 | 04.08.61.591.2 | AWG5 (16 mm2) | SOL4-O-C2 | SOLC37-5-2 | C-side | Bended lug M6 on LVPS side; straight lug M8 ?? in LV filter box | 1 | 0 | 25 (tbc) | N | 0 | N | N | N | 1 cable = 2 LV 16 mm2 + 2 ground 16 mm2; length is approximative; additional cable between LVPS and SOLAR crate
69 | MCH | LV FEC | 8 | 100 | 04.08.61.591.2 | AWG5 (16 mm2) | SOL4-O-C3 | SOLC37-5-3 | C-side | Bended lug M6 on LVPS side; straight lug M8 ?? in LV filter box | 1 | 0 | 25 (tbc) | N | 0 | N | N | N | 1 cable = 2 LV 16 mm2 + 2 ground 16 mm2; length is approximative; additional cable between LVPS and SOLAR crate
70 | MCH | LV FEC | 8 | 100 | 04.08.61.591.2 | AWG5 (16 mm2) | SOL4-O-C4 | SOLC38-1-1 | C-side | Bended lug M6 on LVPS side; straight lug M8 ?? in LV filter box | 1 | 0 | 25 (tbc) | N | 0 | N | N | N | 1 cable = 2 LV 16 mm2 + 2 ground 16 mm2; length is approximative; additional cable between LVPS and SOLAR crate
71 | MCH | LV FEC | 8 | 100 | 04.08.61.591.2 | AWG5 (16 mm2) | SOL5-O-C1 | SOLC38-2-1 | C-side | Bended lug M6 on LVPS side; straight lug M8 ?? in LV filter box | 1 | 0 | 20 (tbc) | N | 0 | N | N | N | 1 cable = 2 LV 16 mm2 + 2 ground 16 mm2; length is approximative; additional cable between LVPS and SOLAR crate
75 | MCH | LV FEC | 8 | 100 | 04.08.61.591.2 | AWG5 (16 mm2) | SOL5-O-C5 | SOLC38-3-1 | C-side | Bended lug M6 on LVPS side; straight lug M8 ?? in LV filter box | 1 | 0 | 20 (tbc) | N | 0 | N | N | N | 1 cable = 2 LV 16 mm2 + 2 ground 16 mm2; length is approximative; additional cable between LVPS and SOLAR crate
76 | MCH | LV FEC | 8 | 100 | 04.08.61.591.2 | AWG5 (16 mm2) | SOL6-O-C1 | SOLC38-3-2 | C-side | Bended lug M6 on LVPS side; straight lug M8 ?? in LV filter box | 1 | 0 | 20 (tbc) | N | 0 | N | N | N | 1 cable = 2 LV 16 mm2 + 2 ground 16 mm2; length is approximative; additional cable between LVPS and SOLAR crate
80 | MCH | LV FEC | 8 | 100 | 04.08.61.591.2 | AWG5 (16 mm2) | SOL6-O-C5 | SOLC38-3-4 | C-side | Bended lug M6 on LVPS side; straight lug M8 ?? in LV filter box |  | 0 | 20 (tbc) | N | 0 | N | N | N | 1 cable = 2 LV 16 mm2 + 2 ground 16 mm2; length is approximative; additional cable between LVPS and SOLAR crate
81 | MCH | LV FEC | 8 | 100 | 04.08.61.591.2 | AWG5 (16 mm2) | SOL7-O | SOLC38-5-1 | C-side | Bended lug M6 on LVPS side; connector BURNDY 4 pins (for 16 mm2 cable) | 1 | 0 | 15 (tbc) | N | 0 | N | N | N | 1 cable = 2 LV 16 mm2 + 2 ground 16 mm2; length is approximative; additional cable between LVPS and SOLAR crate
87 | MCH | LV FEC | 8 | 100 | 04.08.61.591.2 | AWG5 (16 mm2) | SOL7-O | SOLC38-1-2 | C-side | Bended lug M6 on LVPS side; connector BURNDY 4 pins (for 16 mm2 cable) | 1 | 0 | 15 (tbc) | N | 0 | N | N | N | 1 cable = 2 LV 16 mm2 + 2 ground 16 mm2; length is approximative; additional cable between LVPS and SOLAR crate
88 | MCH | LV FEC | 8 | 100 | 04.08.61.591.2 | AWG5 (16 mm2) | SOL8-O | SOLC38-1-3 | C-side | Bended lug M6 on LVPS side; connector BURNDY 4 pins (for 16 mm2 cable) | 1 | 0 | 15 (tbc) | N | 0 | N | N | N | 1 cable = 2 LV 16 mm2 + 2 ground 16 mm2; length is approximative; additional cable between LVPS and SOLAR crate
94 | MCH | LV FEC | 8 | 100 | 04.08.61.591.2 | AWG5 (16 mm2) | SOL8-O | SOLC38-2-5 | C-side | Bended lug M6 on LVPS side; connector BURNDY 4 pins (for 16 mm2 cable) | 1 | 0 | 15 (tbc) | N | 0 | N | N | N | 1 cable = 2 LV 16 mm2 + 2 ground 16 mm2; length is approximative; additional cable between LVPS and SOLAR crate
95 | MCH | LV FEC | 8 | 100 | 04.08.61.591.2 | AWG5 (16 mm2) | SOL9-O | SOLC39-3-1 | C-side | Bended lug M6 on LVPS side; connector BURNDY 4 pins (for 16 mm2 cable) | 1 | 0 | 15 (tbc) | N | 0 | N | N | N | 1 cable = 2 LV 16 mm2 + 2 ground 16 mm2; length is approximative; additional cable between LVPS and SOLAR crate
102 | MCH | LV FEC | 8 | 100 | 04.08.61.591.2 | AWG5 (16 mm2) | SOL9-O | SOLC39-4-2 | C-side | Bended lug M6 on LVPS side; connector BURNDY 4 pins (for 16 mm2 cable) | 1 | 0 | 15 (tbc) | N | 0 | N | N | N | 1 cable = 2 LV 16 mm2 + 2 ground 16 mm2; length is approximative; additional cable between LVPS and SOLAR crate
103 | MCH | LV FEC | 8 | 100 | 04.08.61.591.2 | AWG5 (16 mm2) | SOL10-O | SOLC39-4-3 | C-side | Bended lug M6 on LVPS side; connector BURNDY 4 pins (for 16 mm2 cable) | 1 | 0 | 15 (tbc) | N | 0 | N | N | N | 1 cable = 2 LV 16 mm2 + 2 ground 16 mm2; length is approximative; additional cable between LVPS and SOLAR crate
110 | MCH | LV FEC | 8 | 100 | 04.08.61.591.2 | AWG5 (16 mm2) | SOL10-O | SOLC39-5-5 | C-side | Bended lug M6 on LVPS side; connector BURNDY 4 pins (for 16 mm2 cable) | 1 | 0 | 15 (tbc) | N | 0 | N | N | N | 1 cable = 2 LV 16 mm2 + 2 ground 16 mm2; length is approximative; additional cable between LVPS and SOLAR crate
MCH sense FEC INSIDE???
Note on P26: Total from racks up to A side (MFTPP1)
Note on P30: Total from racks up to A side (MFTPP1)

## Sheet2
| Racks allocated | Cable section defined (AWG) | Cable type(s) defined | Connectors defined | Routing defined | Remarks
ITS | Keep ITS A-side racks | Y | N | N | Y | Currenlty investigating different possibilities
TPC | No change | Y | Y | Y | Y | Prototype installed in TS1
MFT | Y | Y | N | N | Y
FIT-T0 | Y | Y | Y | N | N | Routing of signal cables requires test during YETS
FIT-V0 | Y | Y | Y | N | Y
CPV | Y | Y | Y | Y | Y
ZDC | No change | Y | N | N | N