## Slide 1: Personnel Protection Systems New control solutions for safety applications
F. Valentini (BE-ICS-CSE)
KT – Innovation Day – 26th October 2018

## Slide 2: Personnel Protection Systems @ CERN
1
2
3
4
5
Risk Assessment
All hazards are analyzed and all possible accident scenarios identified.
Safety Instrumented Functions
System Architectural Design
PLC Code Development & Cabinets
Site Installation & Commissioning
DOMAIN OF OUR
PROPOSITION
The system’s automatic safety actions are translated into mathematical Boolean formulas.
All safety components and the logic controller are chosen and the detailed design is finalized.
The logic controller (PLC) is programmed and extensively tested. The electrical cabinet is mounted.
All mounting and cabling works on site are realized. The electrical cabinet is connected and final commissioning /DSO tests performed.
Development Process

## Slide 3: Personnel Protection Systems @ CERN
Small/Medium size
Safety Systems
Experimental Areas
Few communicating rooms hosting radiological hazards.
MEDICIS LAB
Small bunker with 1 only access door and few hazardous equipment inside.
ADAM-LIGHT
Small rooms with 1 or 2 access doors and max 5 class-4 lasers.
LASER ROOMS
TEN similar installations are expected per year !
Our proposition intends to help dealing more efficiently with this type of installations by reducing development and maintenance costs related to the logic controller part.

## Slide 4: Example: GBAR Laser Room Installation
Inputs: 21 Outputs: 10
Outsourcing cost for the cabinet: 30K CHF

## Slide 5: Our Primary Objective
Make Affordable Safety
A safety system can effectively reduce damages to personnel operating in hazardous situations. The cost of the system shall be then considered as an investment that shall however remain reasonably proportional to the Value at Risk.
Reduce Costs for Material & Installations
The material costs for controllers and cabinets cabling are often prohibitive for small size experimental facilities funded by universities or other institutions.
Solution Compliant with SIL-2/3 Requirements
The conformity on any electrical / electromechanical device related to personnel safety shall be proven against the IEC-61508 standard.
No Specific Software Development
A model of development where any PPS installation has its own version of safety software can become unsustainable after few dozens of instances.
Minimal Maintenance
Minimize the decay of resources that, year after year, remain blocked into maintenance tasks.
IEC

## Slide 6
Our Proposition
Acknowledgments:
University Federico II (Naples)

## Slide 7: The R&D Activity: basic concept
Remote Monitoring
Lookup Table
MTTF: 3’441 Years
10 Years data retention
Very Simple Logic Solver

## Slide 8
The R&D Activity: first prototype
16 Digital Inputs
8 Digital Outputs
24V

## Slide 9: Development Milestones
I
II
III
Add new features:
+GPIO, Network, local HMI, auto-diagnostic
2019
Identify generic configurable interlock scenarios.
New design & prototyping phase.
Reliability studies, tests & conformity certification
Pilot installation
SIL-3 certified

## Slide 10: Conclusions
Fast return on investment after deployment of 2 small/medium size PPS.
Potential applications for renovation of SPS North EXP Areas, 60 Laser rooms and other small facilities @ CERN.
Other areas of application outside CERN
  Medical sector: interlock of radiological treatment rooms;
  Other research laboratories: Alba, ITER, etc.
  Industrial sector: interlock of hazardous machinery.
Our proposition allows to:
  Build compact boxes for mural fixation;
  Eliminate costs for big cabinets design, cabling and PLC programming;
  Reduce sensibly the maintenance works.

## Slide 12: Personnel Protection Systems @ CERN
Large size accelerator Complexes (as LHC, PS, SPS)

## Slide 13: Small/Medium Size PPS (Experimental Areas)
MEDICIS LAB
ADAM-LIGHT Exp
TEN similar installations are requested per year to BE/ICS !

## Slide 14: Main Limitations of PLC solutions
Cost of Material: approx. 2’500 CHF for Siemens parts.
Production Time: 1 staff engaged for min 2 weeks (1w cabinet mounting, 1w SW development & testing).
Maintenance Costs: dozens of PLCs with different SW to be kept updated.
Siemens Update Policy: annual new releases of PLC firmware and development software impacts on operation of the experiments.
Siemens PLC 1200 Safety series
+
Siemens Simatic Panel
Most Basic PLC Configuration:

## Slide 15: Other available options: two products of interest
Lasermet ICS-6
National Instruments 9350
IEC 60825
Laser safety standard
No Software.
Prebuild interlock logic based on relays.
Compact practical
solution for mural installation.
Disadvantages
Interlock logic performed by a reprogrammable FPGA
Certified only against laser safety standard.
Too limited prebuild interlock logic.
Very limited I/O space (8DI / 8DO) & no com between modules.
Expensive: more than 1’000 usd.
Remote monitoring NOT possible.
Remote monitoring only if integrated in a cRIO chassis.

## Slide 16: Other available options: FPGAs
Microsemi FPGA
High level of reliability.
Proven in automotive and space applications.
Wide range of
Interfaces, including Ethernet.
Allows to deploy
compact custom solutions.
Disadvantages
Specific techniques of redundant programming shall be adopted.
Integration in a custom PCB more complex: longer dev times.
A certification against iec-61508 is not available.
Programming environment not certified against iec-61508.

## Slide 17: The R&D Activity: basic idea
MTTF: 3’441 Years
16 INPUTS
8 OUTPUTS
10 Years data retention
IF [Premise] THEN [Action]
Simple Boolean Logic Computation
Lookup Table

## Slide 18: The R&D Activity: software part
(1) Logic Specification
(2) Logic Simulation
(4) Exhaustive Testing
(3) Memory Flashing