## Slide 2
R2E Annual Meeting 2018
Radiation tolerant developments: Cryogenics
Juan Casas & Nikolaos Trikoupis
CERN TE-CRG
Cryogenic Instrumentation
TE-CRG-CI
https://indico.cern.ch/event/760345/
11 DEC 2018

## Slide 3: Contents
Industrial/Commercial equipment.
Rad-hard instrumentation.
  Radiation hardness of the LHC valve actuators.
Custom rad-tol electronics.
  Results from recent tests.
R2E strategy.
Cryogenic Instrumentation
TE-CRG-CI

## Slide 4: Industrial/Commercial equipment
Commercial equipment in safe/protected areas, mainly:
Industrial Programmable Logic Controllers (PLCs).
PLC associated components (IO, field electronics, ...).
Intelligent valve positioner: active electronics.
Cold Compressor electronics.
…
P4/P8: Already relocated.
P2: No relocation required.
P6 @ UX65. Low rad levels. No R2E failures ever observed (2015 used as benchmark), no relocation planned.
No relocation foreseen for HiLumi.
Cryogenic Instrumentation
TE-CRG-CI

## Slide 5: Radiation hard Instruments
Qualified or intrinsically rad-hard instruments:
Temperature sensors (tested @ cold till 3 x 1014 n.cm-2).
Pressure sensors measuring > 1 bar.
Superconducting level gauges.
Solenoid valves.
………
Valve Positioner:
Radiation test: Co-60 gamma source.
Over 10 piezo tested: 1st failure @ 137 kGy TID. Overall test up to 280 kGy.
In-situ radiation monitoring: lower doses than expected from simulations.
Pressure sensor:
Low range pressure sensors required by LHC and experiments.
Qualified supplier: none @ present!
Candidate devices being evaluated.
Presentation “Radiation Hardness of Pressure Sensors Suitable to Measure in the 0-100mbar Range”, by Michal Jozef Les on 12 Dec 2018 18:20.
Results in the next slides .
Cryogenic Instrumentation
TE-CRG-CI

## Slide 6
Radiation hardness of the LHC valve actuators
Cryogenic Instrumentation
TE-CRG-CI

## Slide 7
Radiation hardness of the LHC valve actuators
HiLumi radiation estimation shall not exceed 60 kGy for worst location
Gamma rays dose: SIPART qualified for HiLumi
However is the gamma radiation equivalent to a mixed field that include heavy particles?
60 kGy TID target difficult to reach in CHARM
* Eventually single piezo test in HIRRAD?
Cryogenic Instrumentation
TE-CRG-CI

## Slide 8: Custom rad-tol equipment - The cryogenics crate
The cryogenics crate
For the LHC:
800 WorldFIP crates
Active channels:
6500 Temperature
800 Pressure
500 Liquid He level gauges
1400 Cold mass heaters
600 Beam screen heaters
1100 Mechanical Switches (I/O)
1050 WorldFIP cards (2100 channels)
Installed in ARCs (from cell 8), shielded and protected areas.
All existing designs based on Microsemi antifuse A54SX FPGA (3 kGy).
Rad-tol target for electronic components > 1kGy.
System architecture
Cryogenic Instrumentation
TE-CRG-CI

## Slide 9: Cards with Smartfusion2 FPGA 2016/2017/2018
Prototype double-channel LT card
3 cards with FPGA code version Hamming 8/4***, TMR
During 2016 the 4 FPGA versions were explored:
Onehot*/Safe, No TMR**
Onehot/Safe, TMR
Hamming 8/4***, TMR
Hamming 8/4, TMR with with distant FFs
*Onehot: FSM encoding with only one “1” bit per state.
**TMR: Triple Modular Redundancy on FFs only.
***Hamming 8/4: Double error detect single error correct.
All versions offered 13-bit diagnostics per channel.
Prototype double-channel temperature card
Cryogenic Instrumentation
TE-CRG-CI

## Slide 10: Cards with Smartfusion2 FPGA – Some results
Testing cards with new reprogrammable FPGA
Approximately 1 automatic action (local or remote) every ~1000 Gy (tunnel).
Observation on the ADC
A new delivery of a long used component (ADC) was found sensitive.
→ Existing productions are OK.
→ To pay attention at future productions.
Anti-latchup circuit to cope with non-destructive SELs.
TID results for all cards/campaigns
Cryogenic Instrumentation
TE-CRG-CI
Paper on Smartfusion2 FPGA under publication: https://edms.cern.ch/document/2050890

## Slide 11: FIP card internal errors – Power consumption
2014/2015
2016
2017
2017: Used cards of previous CHARM tests.
Very high annealing when powered off. All cards are still functional.
All 3 irradiation combined TID (Gy)
Cryogenic Instrumentation
TE-CRG-CI

## Slide 12
Example of ongoing unforeseen consolidation.
Metastability problem on the antifuse TT FPGAs. For 2019.
CLK
“ADC Busy” after FF
“ADC Busy” before FF
Problem solved after synchronizing the busy signal
Tested at 2 spiky cards removed from the tunnel.
Noisy when original card; no noise with extra FF.
Example of flex PCB solution
Estimated cost: < 10 CHF
Location on the TT card for flex PCB patch
Currently 115 channels + 80 masked out of ~1100 channels
Radiation test specs ready.
To test around Jan/Feb 19.
Test deployment during LS2.
“Random” erratic behavior seen on some type of cards → Problem understood: FPGA metastability on asynchronous inputs.
So far problem was treated by replacing the FPGA to another “newer” code version that does not suffer from this problem.
FPGA cannot be reprogrammed → Addition of a flip-flop component patch (FF).
Timing violations lead to wrong state in the FPGA statemachine → Reset
Cryogenic Instrumentation
TE-CRG-CI

## Slide 13: AC/DC 24V 50W device TDK-Lambda ZWS50BAF24
Non critical low count ventilator devices installation in shielded areas.
After some failures in LHC, mosfets replaced to rad-tol FCA36N60NF.
After more failures on the modified supplies, the circuit was analysed.
Original power mosfets
Modified power mosfets
Original circuit produces 400 VDC and power mosfets see 475-500 VDC!
After disabling the power factor correction circuit, DC voltage at 325 VDC
And power mosfets see 400 VDC.
Tested units:
#1 Rad-tol Mosfet +47V zener without /PFC
#2 Rad-tol Mosfet without zener/PFC
#3 Rad-tol Mosfet without zener/PFC
#4 Original mosfets without zener/PFC
Failed at:
#1 300 Gy, 1.19 1012 HEH
#2 289 Gy, 1.14 1012 HEH
#3 568 Gy, 2.25 1012 HEH
#4 4 Gy, 1.58 1010 HEH
But finally we will install custom rad-tol linear regulator from crate supply (27 - 33) V to 24 V.
Cryogenic Instrumentation
TE-CRG-CI

## Slide 14: Misc devices/components e.g. 2017
FANs:
Ebmpapst VarioPro 4314/17T (4.8W @ 24V)
Microblow FMA8012BS-M (1.44W @ 12V)
SUNON PF80201V1-000U-A99 (3.42W @ 12V)
OPAs:
OPA132
OPA137
OPA192
OPA129
OPA602 (selected lower cost precision OPA replacement for the OPA627)
AC/DC 24 V 50W Unit (TDK-Lambda ZWS50BAF24)
Cryogenic Instrumentation
TE-CRG-CI

## Slide 15: Rad-Tol: Electronics Strategy
Strategy to cope with failures and radiation effects:
Track power consumption for individual cards/crates to assess TID effects.
Presently done in R1 on 10 crates (72 cards) exposed to low and high TIDs.
On “high” radiation areas leave RadTol crates (<10 over 800) to assess:
  Radiation effects (if any); maximum TID (if ever reached).
  Foresee local cable to relocate equipment
  to middle of cold mass for R7/L7 11T case.
Keep adequate quantity of spare cards and components.
Cards rotation could be option as most cards installed in the ARCs (low TIDs).
Regular maintenance/monitoring is a routine task:
Requests for intervention and corrective actions stored in logbooks.
Long-term signals and diagnostic data in logging database.
Daily automated database queries on a set of pre-defined rules to detect potential problems (Elasticsearch/Kibana).
Rad-tol electronics perform as expected.
(However other lifetime reliability problems might occur earlier).
Cryogenic Instrumentation
TE-CRG-CI

## Slide 16: Summary
Most of the CRG equipment shall perform satisfactorily under HiLumi conditions:
  Radiation tests are performed once/twice per year. Essential to cope with obsolescence and to qualify new devices.
  CRG dedicates already about 0.5 FTE for radiation issues.
Material/devices purchased/scrapped for/after tests: 10 to 30 kCHF/year.
HiLumi: Stay as is; provisionally install cables to relocate cryo-crates for “risk” areas.
Monitoring/diagnostics/maintenance are continuously being applied to all the equipment that is installed in radiation or radiation-free areas.
End of life failures: no indication yet for any equipment (electronics, valve actuator, etc).
Cryogenic Instrumentation
TE-CRG-CI