## Slide 1
An update of dynamic thermal-hydraulic simulations of the JT-60SA cryogenic system for preparing plasma operation
aUniv. Grenoble Alpes, CEA IRIG-d-SBT, Grenoble, 38000, France
bCEA/IRFM Saint-Paul-lez-Durance 13108 France
cFusion for Energy, Broader Approach Program and Delivery Department, Boltzmannstr. 2, D-85748 Garching, Germany
dNaka Fusion Institute, National Institute for Quantum Radiological Science and Technology, 801-1 Mukoyama, Naka, Ibaraki, 311-0193 Japan4
Presented by F. Bonne
S. Varina, F. Bonnea*, C. Hoaa, S. Nicolletb, L. Zanib, J-C Valletb, E. Di Pietroc, K. Fukuid, K. Hamadad, K. Natsumed

## Slide 2: Outline
Introduction
Description of TF loop
Description of the models
Model assumptions
Results & discussion
Conclusion

## Slide 3
Introduction

## Slide 4: JT-60SA Tokamak
    Broader Approach agreement between Europe and Japan
    JT-60SA Tokamak currently under assembly in Naka, Japan
    First plasma operation in 2020

## Slide 5: Acceptance tests of the cryogenic system
Commissioning of the cryogenic system in 2016 with the validation of the pulse operation
5

## Slide 6: Motivations
        Reference scenario 60s/1800 s heat load profile was derived from Vincenta model (2010)
        Updated model with Simcyogenics to prepare the operation with first plasmas
          Cool down scenarios
          Short pulses

## Slide 7
New friction factor for TF is available
 Measured with the cold test facility saclay
Motivations
More realistic new assumptions are made

## Slide 8
Description of TF loop

## Slide 9: Description of TF loop & TF CICC
Description of TF loop & TF CICC
 | TF str | CS str
Length (m) | 18.81 | 7.75
Helium cross-section area (m2) | 1e-4 | 1.963e-5
Number of structures | 18 | 9
Mass per structure (t) | 14.5 | 3.66
Simplified PFD of the TF loop
Characteristics of structures
6 bar
4.4 K
4.9 bar
4.4 K

## Slide 10: Description of TF loop & TF CICC
Description of TF loop & TF CICC
Properties | 
Length (m) | 113
Void fraction (-) | 0.32
Strand diameter (mm) | 0.81
Number of superconducting strands | 324
Number of copper strands | 162
Helium cross-section area (mm2) | 125.8
Wetted perimeter (m) | 1.108
Mass of winding pack (one TF coil) (t) | 5.7
Characteristics of the TF CICC
22 mm
26 mm
Stainless steel jacket
NbTi & Cu strands
Cross-section of the CICC
(Courtesy of S. Nicollet)

## Slide 11
Description of the models

## Slide 12: Description of the models
Vincenta model
Model using the Vincenta code with data available in 2010
Limitations & need for updates :
 New values are now available for friction factor & heat load
 Assumed an uniformly distributed heat load on the CICC
   Ignored the inter-turn thermal coupling
Use Simcryogenics for an updated model

## Slide 13: Description of the models
Simcryogenics model
Schematic of the TF loop

## Slide 14: Description of the models
Simcryogenics model
TF CICC
TF structure
CS structure
cryo-distribution pipes
flow multipliers
Schematic of the branches containing TF CICC & structures

## Slide 15
Model assumptions

## Slide 16: Model assumptions
Friction factor for the CICC
Previous method:
  A form of Katheder correlation proposed by Nicollet et al.
Correlations based on experimental data are now available:
A higher-than-expected pressure drop
 use of a reduced mass flowrate of 3 g/s in the TF CICC
(for TF coil 12: α: [0.09, 0.12], β: [14.3, 49.7], γ: [-0.79, -0.61])

## Slide 17: Model assumptions
Heat transfer coefficient
Previous assumption:
Constant heat transfer coefficient for the TF CICC & structures
(25 W/(m2.K) for the CICC, 750 W/(m2.K) for the structures)
Update by using Dittus-Boelter correlation:
( W/m2.K for the CICC at 3 g/s)
Comparison with Colburn-Reynolds analogy (presented in the paper)
( W/(m2.K) for the CICC at 3 g/s)

## Slide 18: Model assumptions
Heat load
Updated heat load : 14% contingency
Non-uniformly distributed heat load
 | Turn 1 | Turn 2 | Turn 3 | Turn 4 | Turn 5 | Turn 6
distribution | 51% | 21% | 13% | 7% | 4% | 4%

## Slide 19: Model assumptions
Inter-turn thermal coupling
Simplified diagram of one pancake of TF coil
turn 1
turn 2
turn 3
turn 4
turn 5
turn 6
Thermal coupling between the successive turns of the jacket
Calculation of thermal resistance
SS: stainless steel / GE: glass-epoxy
(typical values: 0.69 to 0.72 W/(m.K))
epoxy
22 mm
26 mm
Stainless steel jacket
NbTi & Cu strands
Cross-section of the CICC
inlet
outlet
(Courtesy of S. Nicollet)

## Slide 20
Results and discussion

## Slide 21: Results and discussion
Update of heat load & friction factor
Legend :
Black: Vincenta model / Blue: Simcryogenics model with updated heat load
Magenta: Simcryogenics model with updated heat load & friction factor (=3g/s)

## Slide 22: Results and discussion
Update of heat load & friction factor
Legend :
Black: Vincenta model / Blue: Simcryogenics model with updated heat load
Magenta: Simcryogenics model with updated heat load & friction factor (=3g/s)
Combined updates of heat load & friction factor:
Increase of structure temperature
Longer duration for the CICC outlet temperature to reach its initial value
Decrease of the power received by HX2

## Slide 23: Results and discussion
Inter-turn thermal coupling:
  Experimental test
Experimental setup
(Abdel Maksoud et al. 2015)
Additional test in the Cold Test facility (CTF)
study the effect of the inter-turn thermal coupling
Compare experimental results to simulation results

## Slide 24: Results and discussion
Inter-turn thermal coupling:
  Comparison between the experiment and Simcryogenics model
Outlet temperature after a fast increase of 1K in inlet temperature
 A more consistent model after taking into account the inter-turn thermal coupling

## Slide 25: Results and discussion
Update of heat load & friction factor (a quick reminder of the results)
Legend :
Black: Vincenta model / Blue: Simcryogenics model with updated heat load
Magenta: Simcryogenics model with updated heat load & friction factor (=3g/s)

## Slide 26: Results and discussion
Inter-turn thermal coupling:
  model of the TF loop
Legend :
Black: Vincenta model / Blue: Updated Simcryogenics model with non-uniformly distributed heat load Magenta: Updated Simcryogenics model with non-uniformly distributed heat load & inter-turn thermal coupling

## Slide 27: Results and discussion
Inter-turn thermal coupling: model of the TF loop
Legend :
Black: Vincenta model / Blue: Updated Simcryogenics model with non-uniformly distributed heat load Magenta: Updated Simcryogenics model with non-uniformly distributed heat load & inter-turn thermal coupling
Non-uniformly distributed heat load:
Increase of CICC outlet temperature
Increase of the power received by HX2
Inter-turn thermal coupling:
Decrease of CICC outlet temperature
Decrease of the power received by HX2
Longer duration for the CICC outlet temperature to reach its initial value

## Slide 28: Conclusion
Conclusion
Updates of the model :
With new data available (heat load, friction factor, reduced mass flowrate)
With improvement (non-uniformly distributed heat load, inter-turn thermal coupling)
Profile of the heat load deposited into the thermal buffer:
Different from 2010, mainly due to the update of the heat load, friction factor & =3g/s
Smoother profile
Future applications:
The model can be used:
for preparing plasma operation in the coming years
for being coupled with the cryogenic system
for testing the control strategies related to pulse operation
for investigating cool down scenarios