## Slide 1: Combining Reliability Statistics with Physics of Failure to Study and Simulate the Operational Availability of Redundant Power Converters
Lukas Felsberger
With helpful discussions and inputs from Benjamin Todd, Yves Thurel and Christophe Martin

## Slide 2: Contents
Problem statement
Method
Example
  CIBD simulation
Summary and Conclusions

## Slide 3: Last time…
Three rules to achieve fault tolerance
Redundancy and fault isolation
  Avoid single point, common or cascading failures
  By separation, variation, protection ….
Fault localization and diagnosis
Fault notification and on-line repair

## Slide 4: Problem statement
Given a redundant system and its inherent failure modes:
What’s the chance of simultaneous failure within a certain repair duration?
What’s the cost of ownership?
What’s the cost to the organization due to system downtime (due to simultaneous failures)?
For different possible operational modes – Load sharing (50:50) vs hot-spare (100:0) vs something in-between (x:y):

## Slide 5: In the literature…
Simple analytic models based on constant failure rates
Methods for non-constant failure modes with simple load sharing assumptions and no consideration of multiple failure modes or failure mechanisms

## Slide 6: Method
Starting point:
  k oo n Redundant system composed of units (here 1 oo 2)
  Each unit has set of competing failure modes
    We have an idea of each failure mechanism (PoF)
Unit 1
Unit 2

## Slide 7: Method – Modeling degradation
Operational time/cycles
Material strength -/
Stress - -
Failures
McPherson, Joe W. Reliability physics and engineering. New York: Springer, 2010.

## Slide 8: Method – Modeling degradation
Operational time/cycles
Material strength -/
Stress - -
Load
McPherson, Joe W. Reliability physics and engineering. New York: Springer, 2010.
Notes: TTF models usually follow power law or exponential model  same for acceleration factor
If acceleration is carried out properly  beta does not change

## Slide 9: Method – Acceleration factors
The acceleration of a failure depends on its mechanism
Temperature driven?
Humidity driven?
Voltage driven?
Combined drivers?
Failure drivers:
Failure drivers:
Failure drivers:
Failure drivers:

## Slide 10: Method – Load Sharing Modeling
The deceleration of a failure due to redundancy depends on its mechanism
Temperature driven?
Humidity driven?
Voltage driven?
Combined drivers?
System Load:
System Load:
𝐿 ̃
Load on unit under Load Sharing Policy :
Load on unit U_i under Load Sharing Policy 𝐿𝑆𝑃:
𝐿_𝑖=𝐿𝑆𝑃_𝑖 (𝐿 ̃)
Stress for failure mode on unit :
Stress for failure mode 𝑗 on unit 𝑖:
𝝃_(𝒊,𝒋) (𝐿𝑆𝑃_𝑖 (𝐿 ̃))
Acceleration factor for failure mode on unit :
Acceleration factor for failure mode 𝑗 on unit U_i:
𝐴𝐹_(𝑖,𝑗) (𝝃_(𝒊,𝒋),𝝃_𝒓𝒆𝒇)

## Slide 11: Method – Cumulative Damage Model
Notes: TTF models usually follow power law or exponential model  same for acceleration factor
If acceleration is carried out properly  beta does not change

## Slide 12: Method – Simulation
Having a system with known
  Failure modes
  Their load dependent acceleration factors
the system operation can be simulated:
System 1
System 2

## Slide 13: Method - Simulation

## Slide 14: Method - Simulation

## Slide 15: Contents
Problem statement
Method
Example
  CIBD simulation
Summary and Conclusions

## Slide 16: Example - CIBD
Three failure modes
Fuse
Other (not closer studied)
Capacitor wear-out
Operated at three load levels
 Consider as accelerated testing

## Slide 17: Example - CIBD
For each failure mode
Determine failure mechanism
Determine acceleration factor

## Slide 18: Example – CIBD – Fuse failure mode
Literature:
Mechanical wear out due to thermal cycling
  Switching ON/OFF (low frequency)
  AC (high frequency)
Critical stressor
Acceleration factor:
Meng, X. Z., and J. G. J. Sloot. "Reliability concept for electric fuses." IEE Proceedings-Science, Measurement and Technology 144.2 (1997): 87-92.

## Slide 19: Example – CIBD – Fuse failure mode
Fitting (weight according to #fail) power law model gives:
Acceleration factor:
(Comment: Data hints at multiple failure modes.)
 | I [A] | #fail
Dev 1 | 0.2 | 2/95
Dev 2 | 0.45 | 22/605
Dev 3 | 1.2 | 15/145

## Slide 20: Example – CIBD – Failure mode 2
Mix of failure modes suspected
  Acceleration factor model in principle not recommended
Critical stressor is chosen to be the current
Acceleration factor:

## Slide 21: Example – CIBD – Failure mode 2
Fitting (weight according to #fail) power law model gives:
Acceleration factor:
 | I [A] | #fail
Dev 1 | 0.2 | 3/95
Dev 2 | 0.45 | 2/605
Dev 3 | 1.2 | 7/145

## Slide 22: Example – CIBD – Failure mode 3

## Slide 23: Example – CIBD – Failure mode 3
Electrolytic capacitor aging:
Lifetime model:
  Boltzmann constant
  effective activation energy for AL electrolytic capacitor aging
Acceleration Factor:
  Chosen

## Slide 24: Example – CIBD – Failure mode summary

## Slide 25: Example – CIBD– Simulate operation
Three failure modes
Operational lifetime 5000 days
Repair duration
Operational modes
  1:1 (load sharing)
  1:0 (hot spare)
  1:2 (asymmetric sharing)
Cost of repair 150 CHF
Cost of beam abort 200 kCHF
N=106-104 simulations @core level
0.4-3.7A system load @dependency level
100 simulations @UQ level
  Fm1
  Fm2
  Fm3

## Slide 26: Simulation results

## Slide 27: Contents
Problem statement
Method
Example
  Synthetic example
  CIBD simulation
Summary and Conclusions

## Slide 28: Conclusions
There is no general answer for optimal operational mode
  Optimal mode can be determined when
    Failure modes are understood and quantified
    Failure mode acceleration modeling can be applied
Requires data and analysis obtained from
  Accelerated testing or
  Operations and/or
  PoF references
The results shown in this presentation are based on very limited data
  Partially addressed by uncertainty quantification layer
  Further verification necessary
The results are unique for CIBD and not transferable to other power supplies
More details – https://cernbox.cern.ch/index.php/s/tItP1TR0RrSKML1

## Slide 29: Backup slides

## Slide 30: Cost of Beam Abort
CERN budget =1B CHF
  LHC physics is main output
3840 – 4800h physics  200-250k CHF per hour…
assume 50% in stable beams  100kCHF/h
Average turnaround-time: ~2h  200kCHF

## Slide 31: Example – CIBD– Simulate operation
Three failure modes (Yves results)
Operational lifetime 5000 days
Repair duration
Operational modes
  1:1 (load sharing)
  1:0 (hot spare)
  1:2 (asymmetric sharing)
Cost of repair 150 CHF
Cost of beam abort 200 kCHF
N=106-104 simulations @core level
0.4-3.7A system load @dependency level
100 simulations @UQ level
  Fm1
  Fm2
  Fm3

## Slide 32: Simulation results

## Slide 33: Example – CIBD– Simulate operation
Three failure modes
Operational lifetime 5000 days
Repair duration
Operational modes
  1:1 (load sharing)
  1:0 (hot spare)
  1:2 (asymmetric sharing)
Cost of repair 150 CHF
Cost of beam abort 200 kCHF
N=106-104 simulations @core level
0.4-3.7A system load @dependency level
100 simulations @UQ level
  Fm1
  Fm2
  Fm3

## Slide 34: Simulation results

## Slide 35: Example – CIBD – Fuse failure mode
 | I [A] | #fail | [d] |  | [d] |  | [d] | 
Dev 1 | 0.2 | 2/95 | 147k | 1 (Weibayes) | 87k | 1.16 | 35k | 1.6 (Weibayes)
Dev 2 | 0.45 | 22/605 | 105k | 0.92 | 50k | 1.16 | 23k | 1.6 (Weibayes)
Dev 3 | 1.2 | 15/145 | 9830 | 1.8 | 19k | 1.16 | 11k | 1.6 (Weibayes)
 | I [A] | #fail |  |  |  |  |  | 
Dev 1 | 0.2 | 2/95 | 147k | 1 (Weibayes) | 87k | 1.16 | 35k | 1.6 (Weibayes)
Dev 2 | 0.45 | 22/605 | 105k | 0.92 | 50k | 1.16 | 23k | 1.6 (Weibayes)
Dev 3 | 1.2 | 15/145 | 9830 | 1.8 | 19k | 1.16 | 11k | 1.6 (Weibayes)
Less than 10% of the population failed
 Estimation quite uncertain

## Slide 36: Example – CIBD – Failure mode 2
 | I [A] | #fail | [d] |  | [d] | 
Dev 1 | 0.2 | 3/95 | 98k | 1 (Weibayes) | 140k | 1.16
Dev 2 | 0.45 | 2/605 | 868k | 1 (Weibayes) | 1577k | 1.16
Dev 3 | 1.2 | 7/145 | 55k | 1.0 | 76k | 1.16
 | I [A] | #fail |  |  |  | 
Dev 1 | 0.2 | 3/95 | 98k | 1 (Weibayes) | 140k | 1.16
Dev 2 | 0.45 | 2/605 | 868k | 1 (Weibayes) | 1577k | 1.16
Dev 3 | 1.2 | 7/145 | 55k | 1.0 | 76k | 1.16
Less than 5% of the population failed
 Estimation very uncertain

## Slide 37: Example – CIBD – Fuse failure mode
Fitting (weight according to #fail) power law model gives:
for separate Weibull fit
for common Weibull fit
for Weibayes fit
Chosen:
Acceleration factor:
(Comment: Data hints at multiple failure modes.)

## Slide 38: Example – CIBD – Failure mode 2
Fitting (weight according to #fail) power law model gives:
for separate Weibull fit
for common Weibull fit
Chosen:
Acceleration factor:

## Slide 39: Failure mode 3 – Generating Failure data
Draw lifetimes from probabilistic TTF model:
TTF model:
  @2.4, 1.2, 0.9, 0.6A ()
  so that a TTF @ 1.2A
Acceleration Factor:
Hall, P. L., and J. E. Strutt. "Probabilistic physics-of-failure models for component reliabilities using Monte Carlo simulation and Weibull analysis: a parametric study." Reliability Engineering & System Safety 80.3 (2003): 233-242.

## Slide 40: Failure mode 3– Generating Failure data
N=145 systems
Failure onset for 1.2A as observed for CIBD
Notes: Would also work for fewer systems

## Slide 41: Failure mode 3 – Obtaining AF
 | I [A] | T [K] | [d] |  | [d] | 
Dev 1 | 2.4 | 343 | 1148 | 7.7 | 1143 | 7.24
Dev 2 | 1.2 | 330 | 4178 | 7.1 | 4183 | 7.24
Dev 3 | 0.9 | 324 | 7363 | 6.9 | 7393 | 7.24
Dev 4 | 0.6 | 317 | 15275 | 7.4 | 15259 | 7.24
 | I [A] | T [K] |  |  |  | 
Dev 1 | 2.4 | 343 | 1148 | 7.7 | 1143 | 7.24
Dev 2 | 1.2 | 330 | 4178 | 7.1 | 4183 | 7.24
Dev 3 | 0.9 | 324 | 7363 | 6.9 | 7393 | 7.24
Dev 4 | 0.6 | 317 | 15275 | 7.4 | 15259 | 7.24
Same
for all distributions
Accelerating the failure mode should leave the (shape) of the Weibull untouched!
 Otherwise we change the failure mechanism and acceleration factor modeling is not possible.

## Slide 42: Failure mode 3 – Obtaining AF
Acceleration factor could be obtained from TTF model.
  Let’s pretend it is unknown
 Fit exponential TTF model:
   obtain: )
 Acceleration model:

## Slide 43: Failure mode 3 – AF
Using current based acceleration model would be misleading
For
 Necessary to know physics of failure

## Slide 44: Example – CIBD– Simulate operation
Comments:
Expected beam aborts are opposite to expected number of replacements
  1:1 has the most beam aborts but the least replacements
  Opposite for 1:0
Failure mode three only “kicks in” for output currents of ~1A
Total cost mostly depends on chosen ratio of cost for replacements vs cost of beam abort

## Slide 45: Example – CIBD – Simulate operation
Three failure modes
Operational lifetime 10000 days
Repair duration
Operational modes
  1:1 (load sharing)
  1:0 (hot spare)
  1:2 (asymmetric sharing)
Cost of repair 150 CHF
Cost of beam abort 200 kCHF
N=106-104 simulations

## Slide 46: Outlook
Current Limitations
  Same cost for all failure modes
  Only two devices
  Stressor dependent only on load of its unit, not other units (e.g. heating from external unit is not considered)
  No switching effects
  No repair efficiency
  No acceleration by multiple factors
Can all be added to the simulation
  But: data and models need to be available

## Slide 47: Contents
Problem statement
Method
Example
  Synthetic example
  CIBD simulation
Summary and Conclusions

## Slide 48: Synthetic Example (inspired by CIBD)

## Slide 49: Synthetic Example (inspired by CIBD)
Electrolytic capacitor aging:
Lifetime model:
  Boltzmann constant
  effective activation energy for AL electrolytic capacitor aging
Acceleration Factor:

## Slide 50: Synthetic Example – Generating Failure data
Draw lifetimes from probabilistic TTF model:
TTF model:
  @2.4, 1.2, 0.9, 0.6A ()
  so that a TTF @ 1.2A
Acceleration Factor:
Hall, P. L., and J. E. Strutt. "Probabilistic physics-of-failure models for component reliabilities using Monte Carlo simulation and Weibull analysis: a parametric study." Reliability Engineering & System Safety 80.3 (2003): 233-242.

## Slide 51: Synthetic Example – Generating Failure data
N=145 systems
Failure onset for 1.2A as observed for CIBD
Notes: Would also work for fewer systems

## Slide 52: Synthetic Example – Obtaining AF
 | I [A] | T [K] | [d] |  | [d] | 
Dev 1 | 2.4 | 343 | 1148 | 7.7 | 1143 | 7.24
Dev 2 | 1.2 | 330 | 4178 | 7.1 | 4183 | 7.24
Dev 3 | 0.9 | 324 | 7363 | 6.9 | 7393 | 7.24
Dev 4 | 0.6 | 317 | 15275 | 7.4 | 15259 | 7.24
 | I [A] | T [K] |  |  |  | 
Dev 1 | 2.4 | 343 | 1148 | 7.7 | 1143 | 7.24
Dev 2 | 1.2 | 330 | 4178 | 7.1 | 4183 | 7.24
Dev 3 | 0.9 | 324 | 7363 | 6.9 | 7393 | 7.24
Dev 4 | 0.6 | 317 | 15275 | 7.4 | 15259 | 7.24
Same
for all distributions
Accelerating the failure mode should leave the (shape) of the Weibull untouched!
 Otherwise we change the failure mechanism and acceleration factor modeling is not possible.

## Slide 53: Synthetic Example – Obtaining AF
Acceleration factor could be obtained from TTF model.
  Let’s pretend it is unknown
 Fit exponential TTF model:
   obtain: )
 Acceleration model:

## Slide 54: Synthetic Example – AF
Using current based acceleration model would be misleading
For
 Necessary to know physics of failure

## Slide 55: Synthetic Example – Simulate operation
One failure mode
Operational lifetime 5000 days
Repair duration
Operational modes
  1:1 (load sharing) -
  1:0 (hot spare) -.
  1:2 (asymmetric sharing) --
Cost of repair 150 CHF
Cost of beam abort 200 kCHF
N=100000 simulations
Notes: Model might not be valid all the way to 4.8A

## Slide 56: Synthetic Example – Simulate operation
Comments:
Expected beam aborts are opposite to expected number of replacements
  1:1 has the most beam aborts but the least replacements
  Opposite for 1:0
Failure mode only “kicks in” for output currents of ~1A
Total cost mostly depends on chosen ratio of cost for replacements vs cost of beam abort
  Depending on output current each mode can be the most economic
Notes: Model might not be valid all the way to 4.8A

## Slide 57: Synthetic Example – Simulate operation
One failure mode
Operational lifetime 10000 days
Repair duration
Operational modes
  1:1 (load sharing)
  1:0 (hot spare)
  1:2 (asymmetric sharing)
Cost of repair 150 CHF
Cost of beam abort 200 kCHF
N=100000 simulations

## Slide 58: Redundancy – Load distribution
Thought experiment
Imagine two sub systems. Both have one wear out failure mode
  Load sharing (50:50) operation: At the time that device #1 fails, device #2 is likely to fail as well
  Hot spare operation (100:0): At the time that device #1 fails, device #2 is unlikely to fail (as good as new)

## Slide 59: Redundancy – Load distribution
Considering wear-out the load distribution does affect the chance of simultaneous failure:
Simple to give qualitative answer for a single failure mode
  In reality we have a mix of failure modes, different wear-out “drivers” and need quantitative answers
 This calls for a simulation

## Slide 60: Reliability concepts
Physics of Failure
Studies failure mechanisms
Power supplies
Somewhere in between
Reliability statistics
Studies failure probabilities of systems
Mathematics/Statistics
Relevant for e.g. semiconductor industry
Physics, Materials Science,…
Relevant for e.g. reliability study of large projects
For some problems it is sufficient to look at failure rates, for others we need to fully understand the failure mechanism and physics
Failure mode thinking
System component thinking

## Slide 61: Failure mode “thinking”
Flowchart depicts the cycle of failure modes in systems
Reliability block diagrams can be misleading
  Failure modes do not stay within one “block”
  FTA is more intuitive in certain cases

## Slide 62: Situation at TE-EPC
Budget and time limitations (obviously)
Most systems are built with externally fabricated components (COTS)
  Coming without accurate reliability specification
  Source of uncertainty
Systems are designed (or reviewed) by experienced engineers
  Reliability data shows little evidence for major design flaws
Many efforts are already invested in increasing the reliability and availability
  Experience in designing, manufacturing and operating power converters
  Redundancy
  Equipment monitoring and “smart” maintenance
  …

## Slide 63: Redundancy – Load distribution
What’s the chance of simultaneous failure within a certain repair duration?
Assuming constant failure rates the load distribution does not affect the chance of simultaneous failure
Considering wear-out the load distribution does affect the chance of simultaneous failure

## Slide 64: Redundancy – Load distribution
Simulation study
Will put a super short explanation

## Slide 65: Simulation study - discussion
Depending on failure modes and operational parameters one load-sharing scheme is optimal
  Can be determined with data from
    Accelerated testing
    Past operation