## Slide 1: DFH : Individual Vs parallel hydraulic circuits
2 principles:
  Individual : Splices, HTS & Current Leads cooled in series
  Parallel : Splices cooled in parallel hydraulic circuits
Many assumptions…
 figures & concrete applications…
  Ratio ?
  Compare the consequences of increasing the mass flow locally around one splice
Functions: | Individual | Parallel
Control principle: | Current lead valve controls Tsplice & TCL Bypass valve adjusts DFH inlet temperature | Current lead valve controls TCL Bypass valve controls highest of Tsplice
Transient phases: Cool down / Warm up Ramp up / down | Mass flow through bypass main flowing section Change of mass flow distribution bypass-CL | Mass flow around splices Identical pressure for all CL circuits inlets
 | Apparent Advantages: 1 splice = 1 Valve (easy to target one splice) Easy control if CL needs >> splice or HTS needs Big bypass diameter for transients and control of | Apparent Advantages: Independent control of and CL mass flows only adjusted to CL needs Splices needs covered by bypass (if > to CL needs)
 | Apparent Drawbacks: CL mass flow dependent from splice needs Bypass mass flow can not increase heat extraction Mass flow distribution evolves during Ramp up | Apparent Drawbacks: Difficulties to ensure equal flows in parallel circuits from design Increasing mass flow around one splice  high total mass flow increase
Functions: | Individual | Parallel
Control principle: | Current lead valve controls Tsplice & TCL Bypass valve adjusts DFH inlet temperature | Current lead valve controls TCL Bypass valve controls highest of Tsplice
Transient phases: Cool down / Warm up Ramp up / down | Mass flow through bypass main flowing section Change of mass flow distribution bypass-CL | Mass flow around splices Identical pressure for all CL circuits inlets
 | Apparent Drawbacks: CL mass flow dependent from splice needs Bypass mass flow can not increase heat extraction Mass flow distribution evolves during Ramp up | Apparent Drawbacks: Difficulties to ensure equal flows in parallel circuits from design Increasing mass flow around one splice  high total mass flow increase
P1, T1
Pc, Tc
Pa, Ta
P2, T2
P1, T1
P2, T2

## Slide 2: Needs to cool/maintain a 18kA-splice temperature within spec.
3kA splices
Flowing areas
Preliminary early design MgB2-HTS
Chart: Splice temperature for various gaseous temperatures and splice resistances
| 0.25 | 0.5 | 1 | 2.5 | 5 | 7.5 | 10
The=10K, R=10nO | 10.9231 | 10.5294 | 10.3051 | 10.1463 | 10.0841 | 10.0607 | 10.0482
The=10K, R=25nO | 12.3077 | 11.3235 | 10.7627 | 10.3659 | 10.2103 | 10.1519 | 10.1205
The=10K, R=50nO | 14.6154 | 12.6471 | 11.5254 | 10.7317 | 10.4206 | 10.3037 | 10.2411
The=10K, R=100nO | 19.2308 | 15.2941 | 13.0508 | 11.4634 | 10.8411 | 10.6074 | 10.4821
The=15K, R=10nO | 15.8896 | 15.5094 | 15.2935 | 15.141 | 15.081 | 15.0585 | 15.0466
The=15K, R=25nO | 17.2241 | 16.2736 | 15.7337 | 15.3525 | 15.2024 | 15.1463 | 15.1164
The=15K, R=50nO | 19.4481 | 17.5472 | 16.4674 | 15.705 | 15.4048 | 15.2925 | 15.2328
The=15K, R=100nO | 23.8962 | 20.0943 | 17.9348 | 16.4099 | 15.8096 | 15.585 | 15.4655
The=20K, R=10nO | 20.864 | 20.4954 | 20.2857 | 20.1371 | 20.0787 | 20.0569 | 20.0454
The=20K, R=25nO | 22.16 | 21.2385 | 20.7143 | 20.3426 | 20.1968 | 20.1423 | 20.1134
The=20K, R=50nO | 24.32 | 22.4771 | 21.4286 | 20.6853 | 20.3936 | 20.2845 | 20.2269
The=20K, R=100nO | 28.64 | 24.9541 | 22.8571 | 21.3706 | 20.7872 | 20.569 | 20.4538
Current leads requirement range
LHC 13kA current leads mass flow
for:
R18kA=17nΩ (R3Ka=100nΩ)
TGHE=20K
SPLICE PROPERTIES | Unit | Value
Splice length | [mm] | 220
Flowing area Equivalent diameter | [-] [mm] | 6 x ½ DN10 + central DN10 DN20
Deq | [mm] | 20
Heat transfer area | [mm2] | 27600
Dissipated power Current 3kA Resistance | [W] [kA] [nΩ] | From 0 to 5 W 6 X 3 From 10 to 100
Exercise with (very) preliminary design of 18kA splice
Various configurations:
  3 gas temperatures: 10, 15 & 20 K
  4 splice resistances :
    R3kA=10, 25, 50 & 100 nΩ
    Corresponds to
    R18kA=1.5, 4.2, 8.3, 16.7 nΩ
  Constants : I=18 kA, P=1.1 bara
Observations:
  The helium gas temperature has limited influence on the ∆T between gas and splice surface
   TGHE has direct influence on Tsplice
  For low , high TGHE and very high R18kA , the splice temperature remains below 25K.
   The splice will very most likely never need higher mass flow than current leads
  = the current lead mass flow is limited to CL needs
  (for HTS flexible < 15m)
Note: Tbottom CL increases by 0.5 K @ 0.5g/s mass flow per meter of HTS flexible length
Ex: Lflexible HTS= 5 m,
 Tbottom CL =Tc+3 K
Pc, Tc

## Slide 3: Hydraulic studies for parallel flow options
Exercise with DFHx1 and 18kA splice preliminary design: 4 x 18kA splice + 1 path for DFHx2 leads
Observations:
  Most of the flow goes to the biggest Deq circuit
      ≈20% to the 4 splices (5% each) , ≈80% to central outer circuits
   Install upstream orifices for similar parallel mass flows (common practice)
      Order of magnitude : Ø10 mm  Integration of upstream orifices unreliable around MgB2 cables (various Ø, Kapton, solder geometry)
What if:
   A limited diffirence between parallel circuits implies high mass flows unbalance (higher R, Kapton, solder)
      One splice sub-hole is blocked  Atr reduced by 15%  Q reduced by 15%: Non critical
      One splice is warmer  ∆P increase  local mass flow decreases further
      One splice needs twice more heat extraction  total mass flow +150%
      Support and flowing areas obstructions not perfect  mis balance between hydraulic parallel circuits
Chart: Repartition of mass flows in DFHx1 depending on total mass flow
| 2.0539650594377608 | 7.6162870619649912 | 11.30020811554928 | 14.233715249025927 | 16.766214372162622 | 19.036981455267 | 21.118837779240021 | 23.055687508648528 | 24.876484024958 | 26.601544965462605 | 28.245795282119534 | 29.82059082095677 | 31.334816201353071 | 32.795582080814327 | 34.208687471918267 | 35.578937346544478 | 36.910367413928306 | 38.206407283711407 | 39.470001517950649 | 40.703701165257691 | 41.90973414209526
Mass flow per 18kA splice | 0.12223 | 0.44368 | 0.65405 | 0.82074 | 0.96418 | 1.0925 | 1.2099 | 1.319 | 1.4214 | 1.5183 | 1.6105 | 1.6988 | 1.7836 | 1.8654 | 1.9444 | 2.021 | 2.0953 | 2.1677 | 2.2382 | 2.307 | 2.3742
Mass flow per DN40 | 0.78253 | 2.9208 | 4.342 | 5.4754 | 6.4547 | 7.3335 | 8.1396 | 8.8899 | 9.5955 | 10.2643 | 10.9019 | 11.5127 | 12.1002 | 12.6671 | 13.2156 | 13.7475 | 14.2645 | 14.7679 | 15.2587 | 15.7379 | 16.2065
central flowing area :
DN40 38% of total flow
18kA flowing area :
DN20 5% total flow
Ext flowing area :
DN40, 38% of total flow
To CL
To CL
To DFHx2
To CL
To CL
0.5 g/s around one splice  total 7 g/s
1.0 g/s around one splice  total 17 g/s

## Slide 4: Comparison of individual Vs parallel flows for DFH application
For properly designed splices:
  Required mass flow for splices << Required mass flow for CL
Control of mass flows in parallel circuits:
  Difficult for various circuit geometries
Note: independent study, from installation, tooling, transport dimensions arguments.
Individual | Parallel
Apparent Advantages: 1 splice = 1 Valve (easy to target one splice) Easy control if CL needs >> splice or HTS needs Indeed Big bypass diameter for transients and control of 𝑇_(𝐷𝐹𝐻 𝑖𝑛𝑙𝑒𝑡) Present for DFHx2 leads | Apparent Advantages: Independent control of 𝑇_𝑠𝑝𝑙𝑖𝑐𝑒 and 𝑇_𝐶𝐿 CL mass flows only adjusted to CL needs Splice needs in the shadow Splices needs covered by bypass (if > to CL needs) +150%  +20%
Apparent Drawbacks: CL mass flow dependent from splice needs CL needs >> splice needs Bypass mass flow can not increase heat extraction Only feasible if all splices in series Mass flow distribution evolves during Ramp up | Apparent Drawbacks: Difficulties to ensure equal flows in parallel circuits from design Very unreliable Increasing mass flow around one splice  high total mass flow increase upper limit 10 g/s

## Slide 5: Spare info
For 1 kA = 0.05g/s mass flow in CL & THe = 15 K
  @ 18 kA mCL=0.90 g/s  Tsplice = 15.7 K
  @ 13 kA mCL=0.65 g/s  Tsplice = 15.5 K
  @ 2 kA mCL=2x0.10 g/s  Tsplice = 15.5 K
Chart: Splice temperature for various currents
| 0.1 | 0.25 | 0.5 | 1 | 2.5 | 5 | 7.5 | 10
18kA : preliminary design | 18.6986 | 16.7792 | 16.0189 | 15.587 | 15.282 | 15.1619 | 15.117 | 15.0931
13 kA : preliminary design | 16.9292 | 15.9281 | 15.5314 | 15.3062 | 15.1471 | 15.0845 | 15.061 | 15.0486
2 kA : conservative design | 15.7101 | 15.3409 | 15.1961 | 15.1126 | 15.0545 | 15.0311 | 15.0225 | 15.0179
For splices cooled in series by current leads required mass flow:
Tsplice increases with current
= The higher the current, the higher Tsplice
= At 2 kA, low mass flows do not lead to higher Tsplice

## Slide 6
DFHx2 illustration of possible parallel circuits